## Power Cost Calculator
Input Data
Compressor horsepower |  |  |  |  | 100
Motor efficiency |  |  |  |  | 98%
kWh cost |  |  |  |  | 0.07
Hours worked per day |  |  |  |  | 17
Number of days worked in a week |  |  |  |  | 7
Number of weeks worked in a year |  |  |  |  | 52
Total annual hours |  |  |  |  | 6212
Calculated Data
Capacity used | Control type |  | Savings Per Year |  | Control type |  | Savings Per Year |  | Control type |  | Savings Per Year
| MODULATION | LOAD/NO LOAD |  |  | MODULATION | VSD |  |  | LOAD/NO LOAD | VSD
20% | 26811.8794 | 15888.5211 | 10923.3583 | 40.74% | 26811.8794 | 8606.2823 | 18205.5971 | 67.9% | 15888.5211 | 8606.2823 | 7282.2389 | 45.83%
30% | 27142.8903 | 19529.6406 | 7613.2497 | 28.05% | 27142.8903 | 11254.3691 | 15888.5211 | 58.54% | 19529.6406 | 11254.3691 | 8275.2714 | 42.37%
40% | 27473.9011 | 22839.7491 | 4634.152 | 16.87% | 27473.9011 | 13902.456 | 13571.4451 | 49.4% | 22839.7491 | 13902.456 | 8937.2931 | 39.13%
50% | 28135.9229 | 25156.8251 | 2979.0977 | 10.59% | 28135.9229 | 16881.5537 | 11254.3691 | 40% | 25156.8251 | 16881.5537 | 8275.2714 | 32.89%
60% | 28797.9446 | 27142.8903 | 1655.0543 | 5.747% | 28797.9446 | 19529.6406 | 9268.304 | 32.18% | 27142.8903 | 19529.6406 | 7613.2497 | 28.05%
70% | 29790.9771 | 28797.9446 | 993.0326 | 3.333% | 29790.9771 | 22839.7491 | 6951.228 | 23.33% | 28797.9446 | 22839.7491 | 5958.1954 | 20.69%
80% | 30784.0097 | 30121.988 | 662.0217 | 2.151% | 30784.0097 | 25487.836 | 5296.1737 | 17.2% | 30121.988 | 25487.836 | 4634.152 | 15.38%
90% | 31777.0423 | 31115.0206 | 662.0217 | 2.083% | 31777.0423 | 28797.9446 | 2979.0977 | 9.375% | 31115.0206 | 28797.9446 | 2317.076 | 7.447%
100% | 33101.0857 | 33101.0857 | 0 | 0% | 33101.0857 | 34094.1183 | -993.0326 | -3% | 33101.0857 | 34094.1183 | -993.0326 | -3%
Note on B10: PRISMAII:
This information is provided as a quick reference resource and is not intended to serve as a substitute for qualified engineering assistance. While every effort has been made to ensure the accuracy of this information, the results are only approximations based on information received and errors can occur. As such, Air Technologies will not assume any liability for damage, injury or misapplication tied to the use of this information. To see how much energy your factory could save Air Technologies recommends the fitting of an Atlas Copco measuring box to record your air demand over a set period of time, from this we can provide you with a more precise energy savings report.