FORMULAS

Electrical cost = HP x .746 x hours x Kw cost / motor efficiency

Example: 50 hp air compressor that runs 8 hours a day 5 days a week for a year with a $.06 Kw electric rate and a 90% efficient electric motor. 50 hp x .746 x 2080 hours x $.06 / .90 = $5,172.27 per year.

Compressor RPM = motor pulley diameter x motor rpm / compressor pulley diameter.

Gallons= cubic feet / .134

Cubic Feet = gallons x .134

Pump up time (minutes) =

V (tank size) x (final pressure – initial pressure)
7.48 x atmospheric pressure x pump delivery (cfm)

Example: 7.5 hp compressor rated at 24 cfm with an 80 gallon tank – unit starts at 100 psi and turns off at 150 psi.

80 gallons x (150 psi – 100 psi)
7.48 x 14.7 psi x 24 cfm

4,000 = 1.51 minutes 
2,638

Pressure drop and horsepower: Every 1 psi of pressure drop equals 0.5% in horsepower

Heat and horsepower :   Rejected heat from an air-cooled compressor is equal to total machine horsepower x 2,545 BTU per hour

Example: 50 hp compressor with 3 hp fan motor will produce…
53 hp x 2,545 = 134,885 BTU per hour

Note:  This information is provided as a quick reference resource and is not intended to serve as a substitute for qualified engineering assistance.  While every effort has been made to ensure the accuracy of this information, errors can occur.  As such, compressedairgorilla.com will not assume any liability for damage, injury or misapplication tied to the use of this information.