## Machine Selection
[16 empty] | bar | 0
[16 empty] | psi | 1
[16 empty] | °C | 0
[16 empty] | °F | 1
[16 empty] | 50Hz | 0
Increase your air Quality | [7 empty] | FX1-15 |  |  | Quality Air Solutions |  |  |  |  | 60Hz | 1
[16 empty] | l/s | FALSE
Selection Information | [15 empty] | cfm | TRUE
Units of pressure
Units of temperature
Units of flow
Electrical frequency
Inlet Conditions
Ambient temperature | [5 empty] | 77 | °F | 25 | 25 | [5 empty] | K3 | 1
Inlet air temperature | [5 empty] | 95 | °F | 35 | 35 | [5 empty] | K1 - PDP | 0.93875
Inlet pressure | [5 empty] | 101.5 | psi (g) | 70 | 7 | 8 |  |  |  |  | K2 | 1
Inlet flow rate | [5 empty] | 53 | cfm | 25 | 25 | [5 empty] | K1 PDP | 2
| Required PDP |  |  |  |  | 37.4 | °F |  | 3 | [5 empty] | K1 - Machine
| Select machine | [13 empty] | PDP Match | 11
[15 empty] | Machine Match | 5
Performance Data | [14 empty] | K Total | 0.93875
|  | Nominal Conditions |  |  |  |  | Actual Conditions
Type |  | Flow |  |  | PDP | Pressure Drop | Maximum Flow |  |  | PDP | Pressure Drop | Relative Humidity | Air Quality Status |  | LU Flow | 26.6312
|  | l/s | m³/hr | cfm | °F | psi (g) | l/s | m³/hr | cfm | °F | psi (g) | % |  |  | K1 | Row Number
FX 4 |  | 20 | 72 | 42.4 | 37.4 | 3.625 | 18.775 | 67.59 | 39.803 | 37.4 | 3.1945 | 25.82% | No Corrosion | Undersized | 0.93875 | 1 |  | 3
FX 5 |  | 30.4167 | 109.5 | 64.4833 | 37.4 | 4.35 | 28.5536 | 102.7931 | 60.5337 | 37.4 | 3.8334 | 25.82% | No Corrosion | Recommended | 0.93875 | 1 |  | 3
FX 6 |  | 39.1667 | 141 | 83.0333 | 37.4 | 4.64 | 36.7677 | 132.3638 | 77.9475 | 37.4 | 4.089 | 25.82% | No Corrosion | Oversized | 0.93875 | 1 |  | 3
Physical Data
Type |  | Length | Width | Height | Weight | Outlet Connection | Gas | Voltage
|  | mm | mm | mm | Kg
FX 4 |  | 500 | 350 | 484 | 25 | 3/4" | R134a | 115-230/1/60
FX 5 |  | 500 | 350 | 484 | 27 | 3/4" | R134a | 115-230/1/60
FX 6 |  | 500 | 370 | 804 | 51 | 1" | R404A | 115-230/1/60
Use this option to select a dryer to give the required performance
Use this option to see the performance of the dryer in the selected conditions
Recalculation For Specific PDP
Recalculation For Specific P Drop
Correction Factors
FX Dryer Performance & Selection Program
For an explanation of these two columns, click here
Explanation
Click here to learn about
Air Quality
Important Note
FX1-15 50Hz 230V include IEC electrical approval
FX1-15 60Hz 230V are available with either CSA or UL approval
FX1-10 60Hz 115V are available with UL approval
FX1-7 60Hz 115V are available with CSA approval

## Specific PDP
[11 empty] | bar | 0
[11 empty] | psi | 1
[11 empty] | °C | 0
[11 empty] | °F | 1
[11 empty] | 50Hz | 0
Increase your air Quality | [8 empty] | FX1-15 | Quality Air Solutions
Selection Information
Units of pressure
Units of temperature
Electrical frequency
Inlet Conditions
Ambient temperature |  |  |  |  | 77 | °F |  |  |  |  | K3 | 1
Inlet air temperature |  |  |  |  | 95 | °F |  |  |  |  | K1 | 0.93875
Inlet pressure |  |  |  |  | 101.5 | psi (g) |  |  |  |  | K2 | 1
Required PDP |  |  |  |  | 37.4 | °F |  |  |  |  | K1 PDP | 2
[11 empty] | Total | 0.93875
Performance Data
| Nominal Conditions |  |  |  | Actual Conditions
Type | Flow |  |  | Pressure Drop | Flow |  |  | PDP | Pressure Drop
| l/s | m³/hr | cfm | psi (g) | l/s | m³/hr | cfm | °F | psi (g)
FX 1 | 5.8333 | 21 | 12.3667 | 2.175 | 5.476 | 19.7138 | 11.6092 | 37.4 | 1.9167
FX 2 | 10 | 36 | 21.2 | 3.625 | 9.3875 | 33.795 | 19.9015 | 37.4 | 3.1945
FX 3 | 14.1667 | 51 | 30.0333 | 3.625 | 13.299 | 47.8762 | 28.1938 | 37.4 | 3.1945
FX 4 | 20 | 72 | 42.4 | 3.625 | 18.775 | 67.59 | 39.803 | 37.4 | 3.1945
FX 5 | 30.4167 | 109.5 | 64.4833 | 4.35 | 28.5536 | 102.7931 | 60.5337 | 37.4 | 3.8334
FX 6 | 39.1667 | 141 | 83.0333 | 4.64 | 36.7677 | 132.3638 | 77.9475 | 37.4 | 4.089
FX 7 | 50 | 180 | 106 | 5.51 | 46.9375 | 168.975 | 99.5075 | 37.4 | 4.8557
FX 8 | 60 | 216 | 127.2 | 2.61 | 56.325 | 202.77 | 119.409 | 37.4 | 2.3001
FX 9 | 68.3333 | 246 | 144.8667 | 3.625 | 64.1479 | 230.9325 | 135.9936 | 37.4 | 3.1945
FX 10 | 86.6667 | 312 | 183.7333 | 2.61 | 81.3583 | 292.89 | 172.4797 | 37.4 | 2.3001
FX 11 | 108.3333 | 390 | 229.6667 | 2.9 | 101.6979 | 366.1125 | 215.5996 | 37.4 | 2.5556
FX 12 | 128.3333 | 462 | 272.0667 | 3.915 | 120.4729 | 433.7025 | 255.4026 | 37.4 | 3.4501
FX 13 | 165 | 594 | 349.8 | 3.625 | 154.8938 | 557.6175 | 328.3748 | 37.4 | 3.1945
FX 14 | 200 | 720 | 424 | 3.625 | 187.75 | 675.9 | 398.03 | 37.4 | 3.1945
FX 15 | 232 | 835.2 | 491.84 | 5.075 | 217.79 | 784.044 | 461.7148 | 37.4 | 4.4724
FX Dryer Performance Re-Calculation
For Specific PDP
Recalculation For Specific P Drop
Machine Selection
Use this tool to re-size the FX range for a specific set on inlet conditions and for a specific pressure dew point.
Move the slide bars so that the site conditions and required pressure dew point are represented.
This tables shows both the nominal perfomance and actual performance of each dryer based on the specified conditions.
Correction Factors

## Specific P Drop
[11 empty] | bar | FALSE
[11 empty] | psi | TRUE
[11 empty] | °C | FALSE
[11 empty] | °F | TRUE
[11 empty] | 50Hz | FALSE
Increase your air Quality | [8 empty] | FX1-15 | Quality Air Solutions | 60Hz | TRUE
Selection Information
Units of pressure
Units of temperature
Electrical frequency
Inlet Conditions
Ambient temperature |  |  |  |  | 77 | °F | 25 |  |  |  | K3 | 1
Inlet air temperature |  |  |  |  | 95 | °F | 35
Inlet pressure |  |  |  |  | 101.5 | psi (g) | 70 | 7 |  |  | K2 | 1
Acceptable pressure drop |  |  |  |  | 2.9 | psi (g) | 200 | 0.2
Performance Data
| Nominal Conditions |  |  |  | Actual Conditions
Type | Flow |  |  | Pressure Drop | Flow |  |  | Pressure Drop | PDP
| l/s | m³/hr | cfm | psi (g) | l/s | m³/hr | cfm | psi (g) | °F |  |  | K1 | Row No.
FX 1 | 5.8333 | 21 | 12.3667 | 2.175 | 6.7358 | 24.2487 | 14.2798 | 2.9 | 40.1 |  |  | 1.1547 | 16
FX 2 | 10 | 36 | 21.2 | 3.625 | 8.9443 | 32.1994 | 18.9619 | 2.9 | 37.4 |  |  | 0.89443 | 1
FX 3 | 14.1667 | 51 | 30.0333 | 3.625 | 12.6711 | 45.6158 | 26.8626 | 2.9 | 37.4 |  |  | 0.89443 | 1
FX 4 | 20 | 72 | 42.4 | 3.625 | 17.8885 | 64.3988 | 37.9237 | 2.9 | 37.4 |  |  | 0.89443 | 1
FX 5 | 30.4167 | 109.5 | 64.4833 | 4.35 | 24.8351 | 89.4064 | 52.6504 | 2.9 | 37.4 |  |  | 0.8165 | 1
FX 6 | 39.1667 | 141 | 83.0333 | 4.64 | 30.964 | 111.4703 | 65.6436 | 2.9 | 37.4 |  |  | 0.79057 | 1
FX 7 | 50 | 180 | 106 | 5.51 | 36.2738 | 130.5857 | 76.9005 | 2.9 | 37.4 |  |  | 0.72548 | 1
FX 8 | 60 | 216 | 127.2 | 2.61 | 63.2456 | 227.684 | 134.0806 | 2.9 | 39.02 |  |  | 1.0541 | 10
FX 9 | 68.3333 | 246 | 144.8667 | 3.625 | 61.1192 | 220.0291 | 129.5727 | 2.9 | 37.4 |  |  | 0.89443 | 1
FX 10 | 86.6667 | 312 | 183.7333 | 2.61 | 91.3547 | 328.8769 | 193.6719 | 2.9 | 39.02 |  |  | 1.0541 | 10
FX 11 | 108.3333 | 390 | 229.6667 | 2.9 | 108.3333 | 390 | 229.6667 | 2.9 | 38.3 |  |  | 1 | 6
FX 12 | 128.3333 | 462 | 272.0667 | 3.915 | 110.4517 | 397.6263 | 234.1577 | 2.9 | 37.4 |  |  | 0.86066 | 1
FX 13 | 165 | 594 | 349.8 | 3.625 | 147.5805 | 531.2898 | 312.8706 | 2.9 | 37.4 |  |  | 0.89443 | 1
FX 14 | 200 | 720 | 424 | 3.625 | 178.8854 | 643.9876 | 379.2371 | 2.9 | 37.4 |  |  | 0.89443 | 1
FX 15 | 232 | 835.2 | 491.84 | 5.075 | 175.3755 | 631.3519 | 371.7961 | 2.9 | 37.4 |  |  | 0.75593 | 1
Recalculation For Specific PDP
Machine Selection
Correction Factors
FX Dryer Performance Re-Calculation
For Specific Pressure Drop
Use this tool to re-size the FX range for a specific set on inlet conditions and for a specific pressure drop.
Move the slide bars so that the site conditions and acceptable pressure drop are represented.
This tables shows both the nominal perfomance and actual performance of each dryer based on the specified conditions.

## Correction Sheet
Increase your air Quality | [7 empty] | FX1-15 |  |  | Quality Air Solutions
Correction factors for : | [7 empty] | Correction factors for :
Ambient temperature |  |  | 30 | °C |  |  |  | Ambient temperature |  |  | 40 | °C
Inlet pressure |  |  | 7 | bar (g) |  |  |  | Inlet pressure |  |  | 7 | bar (g)
Inlet Temperature
PDP (°C) | Inlet Temperature (°C) | [6 empty] | PDP (°C) | Inlet Temperature (°C) | [6 empty] | Correction factors
| 25 | 30 | 35 | 40 | 45 | 50 | 55 |  | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 1 | 0.8
3 | 1.37 | 1.07 | 0.93875 | 0.8 | 0.65 | 0.55 | 0.44 | 3 | 1.096 | 0.856 | 0.751 | 0.64 | 0.52 | 0.44 | 0.352
5 | 1.57 | 1.24 | 1.1838 | 0.82 | 0.69 | 0.6 | 0.49 | 5 | 1.256 | 0.992 | 0.947 | 0.656 | 0.552 | 0.48 | 0.392
7 | 1.644 | 1.2412 | 1.1561 | 1.01 | 0.81 | 0.74 | 0.62 | 7 | 1.3152 | 0.99296 | 0.92486 | 0.808 | 0.648 | 0.592 | 0.496
10 | 1.8632 | 1.3589 | 1.2471 | 1.11 | 0.96 | 0.86 | 0.7 | 10 | 1.4906 | 1.0871 | 0.99767 | 0.888 | 0.768 | 0.688 | 0.56
Correction factors for : | [7 empty] | Correction factors for :
Ambient temperature |  |  | 30 | °C |  |  |  | Ambient temperature |  |  | 40 | °C
Inlet pressure |  |  | 8 | bar (g) |  |  |  | Inlet pressure |  |  | 8 | bar (g)
PDP (°C) | Inlet Temperature (°C) | [6 empty] | PDP (°C) | Inlet Temperature (°C)
| 25 | 30 | 35 | 40 | 45 | 50 | 55 |  | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 1.03 | 0.824
3 | 1.4111 | 1.1021 | 0.96691 | 0.824 | 0.6695 | 0.5665 | 0.4532 | 3 | 1.1289 | 0.88168 | 0.77353 | 0.6592 | 0.5356 | 0.4532 | 0.36256
5 | 1.6171 | 1.2772 | 1.2193 | 0.8446 | 0.7107 | 0.618 | 0.5047 | 5 | 1.2937 | 1.0218 | 0.97541 | 0.67568 | 0.56856 | 0.4944 | 0.40376
7 | 1.6933 | 1.2784 | 1.1908 | 1.0403 | 0.8343 | 0.7622 | 0.6386 | 7 | 1.3547 | 1.0227 | 0.95261 | 0.83224 | 0.66744 | 0.60976 | 0.51088
10 | 1.9191 | 1.3997 | 1.2845 | 1.1433 | 0.9888 | 0.8858 | 0.721 | 10 | 1.5353 | 1.1197 | 1.0276 | 0.91464 | 0.79104 | 0.70864 | 0.5768
Correction factors for : | [7 empty] | Correction factors for :
Ambient temperature |  |  | 30 | °C |  |  |  | Ambient temperature |  |  | 40 | °C
Inlet pressure |  |  | 10 | bar (g) |  |  |  | Inlet pressure |  |  | 10 | bar (g)
PDP (°C) | Inlet Temperature (°C) | [6 empty] | PDP (°C) | Inlet Temperature (°C)
| 25 | 30 | 35 | 40 | 45 | 50 | 55 |  | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 1.08 | 0.864
3 | 1.4796 | 1.1556 | 1.0138 | 0.864 | 0.702 | 0.594 | 0.4752 | 3 | 1.1837 | 0.92448 | 0.81108 | 0.6912 | 0.5616 | 0.4752 | 0.38016
5 | 1.6956 | 1.3392 | 1.2785 | 0.8856 | 0.7452 | 0.648 | 0.5292 | 5 | 1.3565 | 1.0714 | 1.0228 | 0.70848 | 0.59616 | 0.5184 | 0.42336
7 | 1.7755 | 1.3405 | 1.2486 | 1.0908 | 0.8748 | 0.7992 | 0.6696 | 7 | 1.4204 | 1.0724 | 0.99885 | 0.87264 | 0.69984 | 0.63936 | 0.53568
10 | 2.0123 | 1.4676 | 1.3469 | 1.1988 | 1.0368 | 0.9288 | 0.756 | 10 | 1.6098 | 1.1741 | 1.0775 | 0.95904 | 0.82944 | 0.74304 | 0.6048
Recalculation For Specific P Drop
Machine Selection
Recalculation For Specific PDP
FX Dryer Performance Re-Calculation
Correction Factor Tables

## Air Quality
| Increase your air Quality | FX1-15 | Quality Air Solutions
The Quality Of Air Explained
What Air Quality Is Really Required ?
How Can This Selection Program Help ?
Contrary to what many believe, the PDP of compressed air is not a direct measure of it's quality. PDP is just the temperature at which the water vapour in the air will begin to condense into water droplets.
A direct indicator of the real quality of the compressed air, is it's relative humdity. Relative humidity is the amount of water actually contained in the air, expressed as a percentage of the maximum amount the air can contain before condensation starts.
As an example, if a volume of air contains 25g of moisture, and the same volume has a capacity of 50g of moisture before condensation starts, the relative humidity (RH) of the air will be 50%.
One of the properties of air is that the warmer it becomes, the more water it can hold. This is a very important fact when considering the quality of compressed air and the sizing of refrigerant dryers.
In an ambient condition of 25°C, and using a refrigerant dryer which provides a 3°C PDP, the compressed air has an RH of 26%. This RH directly defines the quality of the air. This means that in provided the compressed air has an RH of 26% in hotter or colder conditions, it has the same quality as air in a 25°C ambient with a PDP of 3°C.
This graph shows the relationship between PDP and ambient temperature for an RH of 26%. As you can see, to get an RH of 26% in a 25°C ambient you need a PDP of 3°C. However, to get the same quality air (RH=26%) in an ambient of 45°C, you only need a PDP of 20°C.
Information and Explanations
In many applications the need to avoid corrosion in pipework, tools and equipment is the overiding factor in the decision to install a refrigernat dryer. The chart below explains the air quality needed to avoid corrosion.
Simply speaking, provided that the RH of the compressed air is below 50%, there is no danger that corrosion will occur.
Above 50% corrosion become possible, and the nearer the RH moves toward 100% the more chance there is that corrosion will start.
Above 100% RH, not only will corrosion begin, the water vapour in the compressed air will start to condense into water droplets, meaning that there will be "free" water in both the pipework and all the tools and machines connected to it.
This means that when sizing a refrigernat dryer, which will be used to eliminate the possibility of corrosion, the important factor is to ensure that in all operating conditions the RH of the compressed air will never climb above 50%. This factor is far more important than selecting a specific PDP, which may or may not provide the air quality required.
This selection tool not will not only select the most appropriate machine for a set of given conditions, it can also calculate how a specific machine will perform in a given set of ambient conditions. Included in the performance table is a column for RH and another for "Air Quality Status" (see diagram below).
The Relative Humdity column shows the RH for the given conditions for the dryer selected. The colour of the cell also changes depending on the value. If the value is 26% or less the cell is green, this means that the compressed air quality is either the same or better than compressed air in an ambient of 25°C with a PDP of 3°C. If above 26% the cell is grey.
The Air Quality Status column shows whether or not the compressed air will cause corrosion in the pipework and tools/machinery connected to it. This cell will also change colour depending on the value. If no corrosion will occur the cell is green, if corrosion could occur it's amber, and if the water vapour will condense, the cell is red.
Machine Selection
Correction Factors
Recalculation For Specific PDP

## Correction Factors (hidden)
Pressure Correction |  |  | Ambient Correction |  | PDP Inlet Correction
Inlet pressure | Correction factor |  | Ambient temperature | Correction factor |  | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | Relevant Column |  | Relevant Column
5 | 0.9 |  | 25 | 1 | 3 | 1.37 | 1.31 | 1.25 | 1.19 | 1.13 | 1.07 | 1.0437 | 1.0175 | 0.99125 | 0.965 | 0.93875 | 0.9125 | 0.88625 | 0.86 | 0.83 | 0.8 | 0.77 | 0.74 | 0.71 | 0.68 | 0.65 | 0.63 | 0.61 | 0.59 | 0.57 | 0.55 | 0.528 | 0.506 | 0.484 | 0.462 | 0.44 | 0.93875 | 2 | 0.93875 | 2
5.1 | 0.906 |  | 26 | 1 | 3.1 | 1.38 | 1.3197 | 1.2594 | 1.1991 | 1.1388 | 1.0785 | 1.0529 | 1.0274 | 1.0018 | 0.97625 | 0.95069 | 0.92512 | 0.89956 | 0.874 | 0.8375 | 0.801 | 0.7712 | 0.7414 | 0.7116 | 0.6818 | 0.652 | 0.6321 | 0.6122 | 0.5923 | 0.5724 | 0.5525 | 0.5305 | 0.5085 | 0.4865 | 0.4645 | 0.4425 | 0.95069 | 3 | 0.95069 | 3
5.2 | 0.912 |  | 27 | 1 | 3.2 | 1.39 | 1.3294 | 1.2688 | 1.2082 | 1.1476 | 1.087 | 1.0621 | 1.0373 | 1.0124 | 0.9875 | 0.96262 | 0.93775 | 0.91287 | 0.888 | 0.845 | 0.802 | 0.7724 | 0.7428 | 0.7132 | 0.6836 | 0.654 | 0.6342 | 0.6144 | 0.5946 | 0.5748 | 0.555 | 0.533 | 0.511 | 0.489 | 0.467 | 0.445 | 0.96262 | 4 | 0.96262 | 4
5.3 | 0.918 |  | 28 | 1 | 3.3 | 1.4 | 1.3391 | 1.2782 | 1.2173 | 1.1564 | 1.0955 | 1.0713 | 1.0471 | 1.0229 | 0.99875 | 0.97456 | 0.95037 | 0.92619 | 0.902 | 0.8525 | 0.803 | 0.7736 | 0.7442 | 0.7148 | 0.6854 | 0.656 | 0.6363 | 0.6166 | 0.5969 | 0.5772 | 0.5575 | 0.5355 | 0.5135 | 0.4915 | 0.4695 | 0.4475 | 0.97456 | 5 | 0.97456 | 5
5.4 | 0.924 |  | 29 | 1 | 3.4 | 1.41 | 1.3488 | 1.2876 | 1.2264 | 1.1652 | 1.104 | 1.0805 | 1.057 | 1.0335 | 1.01 | 0.9865 | 0.963 | 0.9395 | 0.916 | 0.86 | 0.804 | 0.7748 | 0.7456 | 0.7164 | 0.6872 | 0.658 | 0.6384 | 0.6188 | 0.5992 | 0.5796 | 0.56 | 0.538 | 0.516 | 0.494 | 0.472 | 0.45 | 0.9865 | 6 | 0.9865 | 6
5.5 | 0.93 |  | 30 | 1 | 3.5 | 1.42 | 1.3585 | 1.297 | 1.2355 | 1.174 | 1.1125 | 1.0897 | 1.0669 | 1.0441 | 1.0212 | 0.99844 | 0.97562 | 0.95281 | 0.93 | 0.8675 | 0.805 | 0.776 | 0.747 | 0.718 | 0.689 | 0.66 | 0.6405 | 0.621 | 0.6015 | 0.582 | 0.5625 | 0.5405 | 0.5185 | 0.4965 | 0.4745 | 0.4525 | 0.99844 | 7 | 0.99844 | 7
5.6 | 0.936 |  | 31 | 1 | 3.6 | 1.43 | 1.3682 | 1.3064 | 1.2446 | 1.1828 | 1.121 | 1.0989 | 1.0768 | 1.0546 | 1.0325 | 1.0104 | 0.98825 | 0.96613 | 0.944 | 0.875 | 0.806 | 0.7772 | 0.7484 | 0.7196 | 0.6908 | 0.662 | 0.6426 | 0.6232 | 0.6038 | 0.5844 | 0.565 | 0.543 | 0.521 | 0.499 | 0.477 | 0.455 | 1.0104 | 8 | 1.0104 | 8
5.7 | 0.942 |  | 32 | 1 | 3.7 | 1.44 | 1.3779 | 1.3158 | 1.2537 | 1.1916 | 1.1295 | 1.1081 | 1.0866 | 1.0652 | 1.0437 | 1.0223 | 1.0009 | 0.97944 | 0.958 | 0.8825 | 0.807 | 0.7784 | 0.7498 | 0.7212 | 0.6926 | 0.664 | 0.6447 | 0.6254 | 0.6061 | 0.5868 | 0.5675 | 0.5455 | 0.5235 | 0.5015 | 0.4795 | 0.4575 | 1.0223 | 9 | 1.0223 | 9
5.8 | 0.948 |  | 33 | 1 | 3.8 | 1.45 | 1.3876 | 1.3252 | 1.2628 | 1.2004 | 1.138 | 1.1173 | 1.0965 | 1.0757 | 1.055 | 1.0342 | 1.0135 | 0.99275 | 0.972 | 0.89 | 0.808 | 0.7796 | 0.7512 | 0.7228 | 0.6944 | 0.666 | 0.6468 | 0.6276 | 0.6084 | 0.5892 | 0.57 | 0.548 | 0.526 | 0.504 | 0.482 | 0.46 | 1.0342 | 10 | 1.0342 | 10
5.9 | 0.954 |  | 34 | 1 | 3.9 | 1.46 | 1.3973 | 1.3346 | 1.2719 | 1.2092 | 1.1465 | 1.1264 | 1.1064 | 1.0863 | 1.0662 | 1.0462 | 1.0261 | 1.0061 | 0.986 | 0.8975 | 0.809 | 0.7808 | 0.7526 | 0.7244 | 0.6962 | 0.668 | 0.6489 | 0.6298 | 0.6107 | 0.5916 | 0.5725 | 0.5505 | 0.5285 | 0.5065 | 0.4845 | 0.4625 | 1.0462 | 11 | 1.0462 | 11
6 | 0.96 |  | 35 | 1 | 4 | 1.47 | 1.424 | 1.378 | 1.332 | 1.286 | 1.24 | 1.21 | 1.18 | 1.15 | 1.12 | 1.09 | 1.06 | 1.03 | 1 | 0.91 | 0.82 | 0.794 | 0.768 | 0.742 | 0.716 | 0.69 | 0.667 | 0.644 | 0.621 | 0.598 | 0.575 | 0.553 | 0.531 | 0.509 | 0.487 | 0.465 | 1.09 | 12 | 1.09 | 12
6.1 | 0.964 |  | 36 | 1 | 4.1 | 1.48 | 1.4337 | 1.3874 | 1.3411 | 1.2948 | 1.2485 | 1.2193 | 1.1901 | 1.1609 | 1.1318 | 1.1026 | 1.0734 | 1.0442 | 1.015 | 0.918 | 0.821 | 0.7952 | 0.7694 | 0.7436 | 0.7178 | 0.692 | 0.6691 | 0.6462 | 0.6233 | 0.6004 | 0.5775 | 0.5555 | 0.5335 | 0.5115 | 0.4895 | 0.4675 | 1.1026 | 13 | 1.1026 | 13
6.2 | 0.968 |  | 37 | 1 | 4.2 | 1.49 | 1.4434 | 1.3968 | 1.3502 | 1.3036 | 1.257 | 1.2286 | 1.2003 | 1.1719 | 1.1435 | 1.1151 | 1.0868 | 1.0584 | 1.03 | 0.926 | 0.822 | 0.7964 | 0.7708 | 0.7452 | 0.7196 | 0.694 | 0.6712 | 0.6484 | 0.6256 | 0.6028 | 0.58 | 0.558 | 0.536 | 0.514 | 0.492 | 0.47 | 1.1151 | 14 | 1.1151 | 14
6.3 | 0.972 |  | 38 | 1 | 4.3 | 1.5 | 1.4531 | 1.4062 | 1.3593 | 1.3124 | 1.2655 | 1.2379 | 1.2104 | 1.1828 | 1.1553 | 1.1277 | 1.1001 | 1.0726 | 1.045 | 0.934 | 0.823 | 0.7976 | 0.7722 | 0.7468 | 0.7214 | 0.696 | 0.6733 | 0.6506 | 0.6279 | 0.6052 | 0.5825 | 0.5605 | 0.5385 | 0.5165 | 0.4945 | 0.4725 | 1.1277 | 15 | 1.1277 | 15
6.4 | 0.976 |  | 39 | 0.96 | 4.4 | 1.51 | 1.4628 | 1.4156 | 1.3684 | 1.3212 | 1.274 | 1.2472 | 1.2205 | 1.1938 | 1.167 | 1.1402 | 1.1135 | 1.0868 | 1.06 | 0.942 | 0.824 | 0.7988 | 0.7736 | 0.7484 | 0.7232 | 0.698 | 0.6754 | 0.6528 | 0.6302 | 0.6076 | 0.585 | 0.563 | 0.541 | 0.519 | 0.497 | 0.475 | 1.1402 | 16 | 1.1402 | 16
6.5 | 0.98 |  | 40 | 0.8 | 4.5 | 1.52 | 1.4725 | 1.425 | 1.3775 | 1.33 | 1.2825 | 1.2566 | 1.2306 | 1.2047 | 1.1787 | 1.1528 | 1.1269 | 1.1009 | 1.075 | 0.95 | 0.825 | 0.8 | 0.775 | 0.75 | 0.725 | 0.7 | 0.6775 | 0.655 | 0.6325 | 0.61 | 0.5875 | 0.5655 | 0.5435 | 0.5215 | 0.4995 | 0.4775 | 1.1528 | 17 | 1.1528 | 17
6.6 | 0.984 |  | 41 | 0.788 | 4.6 | 1.53 | 1.4822 | 1.4344 | 1.3866 | 1.3388 | 1.291 | 1.2659 | 1.2408 | 1.2156 | 1.1905 | 1.1654 | 1.1402 | 1.1151 | 1.09 | 0.958 | 0.826 | 0.8012 | 0.7764 | 0.7516 | 0.7268 | 0.702 | 0.6796 | 0.6572 | 0.6348 | 0.6124 | 0.59 | 0.568 | 0.546 | 0.524 | 0.502 | 0.48 | 1.1654 | 18 | 1.1654 | 18
6.7 | 0.988 |  | 42 | 0.776 | 4.7 | 1.54 | 1.4919 | 1.4438 | 1.3957 | 1.3476 | 1.2995 | 1.2752 | 1.2509 | 1.2266 | 1.2023 | 1.1779 | 1.1536 | 1.1293 | 1.105 | 0.966 | 0.827 | 0.8024 | 0.7778 | 0.7532 | 0.7286 | 0.704 | 0.6817 | 0.6594 | 0.6371 | 0.6148 | 0.5925 | 0.5705 | 0.5485 | 0.5265 | 0.5045 | 0.4825 | 1.1779 | 19 | 1.1779 | 19
6.8 | 0.992 |  | 43 | 0.764 | 4.8 | 1.55 | 1.5016 | 1.4532 | 1.4048 | 1.3564 | 1.308 | 1.2845 | 1.261 | 1.2375 | 1.214 | 1.1905 | 1.167 | 1.1435 | 1.12 | 0.974 | 0.828 | 0.8036 | 0.7792 | 0.7548 | 0.7304 | 0.706 | 0.6838 | 0.6616 | 0.6394 | 0.6172 | 0.595 | 0.573 | 0.551 | 0.529 | 0.507 | 0.485 | 1.1905 | 20 | 1.1905 | 20
6.9 | 0.996 |  | 44 | 0.752 | 4.9 | 1.56 | 1.5113 | 1.4626 | 1.4139 | 1.3652 | 1.3165 | 1.2938 | 1.2711 | 1.2484 | 1.2257 | 1.2031 | 1.1804 | 1.1577 | 1.135 | 0.982 | 0.829 | 0.8048 | 0.7806 | 0.7564 | 0.7322 | 0.708 | 0.6859 | 0.6638 | 0.6417 | 0.6196 | 0.5975 | 0.5755 | 0.5535 | 0.5315 | 0.5095 | 0.4875 | 1.2031 | 21 | 1.2031 | 21
7 | 1 |  | 45 | 0.74 | 5 | 1.57 | 1.504 | 1.438 | 1.372 | 1.306 | 1.24 | 1.2288 | 1.2175 | 1.2063 | 1.195 | 1.1838 | 1.1725 | 1.1612 | 1.15 | 0.985 | 0.82 | 0.794 | 0.768 | 0.742 | 0.716 | 0.69 | 0.672 | 0.654 | 0.636 | 0.618 | 0.6 | 0.578 | 0.556 | 0.534 | 0.512 | 0.49 | 1.1838 | 22 | 1.1838 | 22
7.1 | 1.003 |  |  |  | 5.1 | 1.5737 | 1.507 | 1.4402 | 1.3735 | 1.3068 | 1.2401 | 1.2285 | 1.217 | 1.2054 | 1.1939 | 1.1824 | 1.1708 | 1.1593 | 1.1478 | 0.98862 | 0.8295 | 0.8028 | 0.7761 | 0.7494 | 0.7227 | 0.696 | 0.6782 | 0.6604 | 0.6426 | 0.6248 | 0.607 | 0.5849 | 0.5628 | 0.5407 | 0.5186 | 0.4965 | 1.1824 | 23 | 1.1824 | 23
7.2 | 1.006 |  |  |  | 5.2 | 1.5774 | 1.5099 | 1.4425 | 1.375 | 1.3076 | 1.2401 | 1.2283 | 1.2165 | 1.2046 | 1.1928 | 1.181 | 1.1692 | 1.1573 | 1.1455 | 0.99225 | 0.839 | 0.8116 | 0.7842 | 0.7568 | 0.7294 | 0.702 | 0.6844 | 0.6668 | 0.6492 | 0.6316 | 0.614 | 0.5918 | 0.5696 | 0.5474 | 0.5252 | 0.503 | 1.181 | 24 | 1.181 | 24
7.3 | 1.009 |  |  |  | 5.3 | 1.5811 | 1.5129 | 1.4447 | 1.3765 | 1.3084 | 1.2402 | 1.2281 | 1.2159 | 1.2038 | 1.1917 | 1.1796 | 1.1675 | 1.1554 | 1.1433 | 0.99587 | 0.8485 | 0.8204 | 0.7923 | 0.7642 | 0.7361 | 0.708 | 0.6906 | 0.6732 | 0.6558 | 0.6384 | 0.621 | 0.5987 | 0.5764 | 0.5541 | 0.5318 | 0.5095 | 1.1796 | 25 | 1.1796 | 25
7.4 | 1.012 |  |  |  | 5.4 | 1.5848 | 1.5159 | 1.447 | 1.3781 | 1.3092 | 1.2402 | 1.2278 | 1.2154 | 1.203 | 1.1906 | 1.1782 | 1.1658 | 1.1534 | 1.141 | 0.9995 | 0.858 | 0.8292 | 0.8004 | 0.7716 | 0.7428 | 0.714 | 0.6968 | 0.6796 | 0.6624 | 0.6452 | 0.628 | 0.6056 | 0.5832 | 0.5608 | 0.5384 | 0.516 | 1.1782 | 26 | 1.1782 | 26
7.5 | 1.015 |  |  |  | 5.5 | 1.5885 | 1.5189 | 1.4492 | 1.3796 | 1.3099 | 1.2403 | 1.2276 | 1.2149 | 1.2022 | 1.1895 | 1.1768 | 1.1641 | 1.1514 | 1.1387 | 1.0031 | 0.8675 | 0.838 | 0.8085 | 0.779 | 0.7495 | 0.72 | 0.703 | 0.686 | 0.669 | 0.652 | 0.635 | 0.6125 | 0.59 | 0.5675 | 0.545 | 0.5225 | 1.1768 | 27 | 1.1768 | 27
7.6 | 1.018 |  |  |  | 5.6 | 1.5922 | 1.5218 | 1.4515 | 1.3811 | 1.3107 | 1.2404 | 1.2274 | 1.2144 | 1.2014 | 1.1884 | 1.1754 | 1.1625 | 1.1495 | 1.1365 | 1.0068 | 0.877 | 0.8468 | 0.8166 | 0.7864 | 0.7562 | 0.726 | 0.7092 | 0.6924 | 0.6756 | 0.6588 | 0.642 | 0.6194 | 0.5968 | 0.5742 | 0.5516 | 0.529 | 1.1754 | 28 | 1.1754 | 28
7.7 | 1.021 |  |  |  | 5.7 | 1.5959 | 1.5248 | 1.4537 | 1.3826 | 1.3115 | 1.2404 | 1.2271 | 1.2139 | 1.2006 | 1.1873 | 1.1741 | 1.1608 | 1.1475 | 1.1342 | 1.0104 | 0.8865 | 0.8556 | 0.8247 | 0.7938 | 0.7629 | 0.732 | 0.7154 | 0.6988 | 0.6822 | 0.6656 | 0.649 | 0.6263 | 0.6036 | 0.5809 | 0.5582 | 0.5355 | 1.1741 | 29 | 1.1741 | 29
7.8 | 1.024 |  |  |  | 5.8 | 1.5996 | 1.5278 | 1.456 | 1.3841 | 1.3123 | 1.2405 | 1.2269 | 1.2134 | 1.1998 | 1.1862 | 1.1727 | 1.1591 | 1.1456 | 1.132 | 1.014 | 0.896 | 0.8644 | 0.8328 | 0.8012 | 0.7696 | 0.738 | 0.7216 | 0.7052 | 0.6888 | 0.6724 | 0.656 | 0.6332 | 0.6104 | 0.5876 | 0.5648 | 0.542 | 1.1727 | 30 | 1.1727 | 30
7.9 | 1.027 |  |  |  | 5.9 | 1.6033 | 1.5307 | 1.4582 | 1.3856 | 1.3131 | 1.2405 | 1.2267 | 1.2128 | 1.199 | 1.1851 | 1.1713 | 1.1574 | 1.1436 | 1.1298 | 1.0176 | 0.9055 | 0.8732 | 0.8409 | 0.8086 | 0.7763 | 0.744 | 0.7278 | 0.7116 | 0.6954 | 0.6792 | 0.663 | 0.6401 | 0.6172 | 0.5943 | 0.5714 | 0.5485 | 1.1713 | 31 | 1.1713 | 31
8 | 1.03 |  |  |  | 6 | 1.607 | 1.5337 | 1.4604 | 1.3872 | 1.3139 | 1.2406 | 1.2265 | 1.2123 | 1.1982 | 1.1841 | 1.1699 | 1.1558 | 1.1416 | 1.1275 | 1.0212 | 0.915 | 0.882 | 0.849 | 0.816 | 0.783 | 0.75 | 0.734 | 0.718 | 0.702 | 0.686 | 0.67 | 0.647 | 0.624 | 0.601 | 0.578 | 0.555 | 1.1699 | 32 | 1.1699 | 32
8.1 | 1.033 |  |  |  | 6.1 | 1.6107 | 1.5367 | 1.4627 | 1.3887 | 1.3147 | 1.2407 | 1.2262 | 1.2118 | 1.1974 | 1.183 | 1.1685 | 1.1541 | 1.1397 | 1.1253 | 1.0249 | 0.9245 | 0.8908 | 0.8571 | 0.8234 | 0.7897 | 0.756 | 0.7402 | 0.7244 | 0.7086 | 0.6928 | 0.677 | 0.6539 | 0.6308 | 0.6077 | 0.5846 | 0.5615 | 1.1685 | 33 | 1.1685 | 33
8.2 | 1.036 |  |  |  | 6.2 | 1.6144 | 1.5397 | 1.4649 | 1.3902 | 1.3155 | 1.2407 | 1.226 | 1.2113 | 1.1966 | 1.1819 | 1.1671 | 1.1524 | 1.1377 | 1.123 | 1.0285 | 0.934 | 0.8996 | 0.8652 | 0.8308 | 0.7964 | 0.762 | 0.7464 | 0.7308 | 0.7152 | 0.6996 | 0.684 | 0.6608 | 0.6376 | 0.6144 | 0.5912 | 0.568 | 1.1671 | 34 | 1.1671 | 34
8.3 | 1.039 |  |  |  | 6.3 | 1.6181 | 1.5426 | 1.4672 | 1.3917 | 1.3162 | 1.2408 | 1.2258 | 1.2108 | 1.1958 | 1.1808 | 1.1658 | 1.1508 | 1.1358 | 1.1207 | 1.0321 | 0.9435 | 0.9084 | 0.8733 | 0.8382 | 0.8031 | 0.768 | 0.7526 | 0.7372 | 0.7218 | 0.7064 | 0.691 | 0.6677 | 0.6444 | 0.6211 | 0.5978 | 0.5745 | 1.1658 | 35 | 1.1658 | 35
8.4 | 1.042 |  |  |  | 6.4 | 1.6218 | 1.5456 | 1.4694 | 1.3932 | 1.317 | 1.2408 | 1.2255 | 1.2103 | 1.195 | 1.1797 | 1.1644 | 1.1491 | 1.1338 | 1.1185 | 1.0357 | 0.953 | 0.9172 | 0.8814 | 0.8456 | 0.8098 | 0.774 | 0.7588 | 0.7436 | 0.7284 | 0.7132 | 0.698 | 0.6746 | 0.6512 | 0.6278 | 0.6044 | 0.581 | 1.1644 | 36 | 1.1644 | 36
8.5 | 1.045 |  |  |  | 6.5 | 1.6255 | 1.5486 | 1.4717 | 1.3947 | 1.3178 | 1.2409 | 1.2253 | 1.2097 | 1.1942 | 1.1786 | 1.163 | 1.1474 | 1.1318 | 1.1162 | 1.0394 | 0.9625 | 0.926 | 0.8895 | 0.853 | 0.8165 | 0.78 | 0.765 | 0.75 | 0.735 | 0.72 | 0.705 | 0.6815 | 0.658 | 0.6345 | 0.611 | 0.5875 | 1.163 | 37 | 1.163 | 37
8.6 | 1.048 |  |  |  | 6.6 | 1.6292 | 1.5516 | 1.4739 | 1.3963 | 1.3186 | 1.241 | 1.2251 | 1.2092 | 1.1933 | 1.1775 | 1.1616 | 1.1457 | 1.1299 | 1.114 | 1.043 | 0.972 | 0.9348 | 0.8976 | 0.8604 | 0.8232 | 0.786 | 0.7712 | 0.7564 | 0.7416 | 0.7268 | 0.712 | 0.6884 | 0.6648 | 0.6412 | 0.6176 | 0.594 | 1.1616 | 38 | 1.1616 | 38
8.7 | 1.051 |  |  |  | 6.7 | 1.6329 | 1.5545 | 1.4761 | 1.3978 | 1.3194 | 1.241 | 1.2249 | 1.2087 | 1.1925 | 1.1764 | 1.1602 | 1.1441 | 1.1279 | 1.1118 | 1.0466 | 0.9815 | 0.9436 | 0.9057 | 0.8678 | 0.8299 | 0.792 | 0.7774 | 0.7628 | 0.7482 | 0.7336 | 0.719 | 0.6953 | 0.6716 | 0.6479 | 0.6242 | 0.6005 | 1.1602 | 39 | 1.1602 | 39
8.8 | 1.054 |  |  |  | 6.8 | 1.6366 | 1.5575 | 1.4784 | 1.3993 | 1.3202 | 1.2411 | 1.2246 | 1.2082 | 1.1917 | 1.1753 | 1.1588 | 1.1424 | 1.1259 | 1.1095 | 1.0502 | 0.991 | 0.9524 | 0.9138 | 0.8752 | 0.8366 | 0.798 | 0.7836 | 0.7692 | 0.7548 | 0.7404 | 0.726 | 0.7022 | 0.6784 | 0.6546 | 0.6308 | 0.607 | 1.1588 | 40 | 1.1588 | 40
8.9 | 1.057 |  |  |  | 6.9 | 1.6403 | 1.5605 | 1.4806 | 1.4008 | 1.321 | 1.2411 | 1.2244 | 1.2077 | 1.1909 | 1.1742 | 1.1575 | 1.1407 | 1.124 | 1.1073 | 1.0539 | 1.0005 | 0.9612 | 0.9219 | 0.8826 | 0.8433 | 0.804 | 0.7898 | 0.7756 | 0.7614 | 0.7472 | 0.733 | 0.7091 | 0.6852 | 0.6613 | 0.6374 | 0.6135 | 1.1575 | 41 | 1.1575 | 41
9 | 1.06 |  |  |  | 7 | 1.644 | 1.5634 | 1.4829 | 1.4023 | 1.3218 | 1.2412 | 1.2242 | 1.2071 | 1.1901 | 1.1731 | 1.1561 | 1.139 | 1.122 | 1.105 | 1.0575 | 1.01 | 0.97 | 0.93 | 0.89 | 0.85 | 0.81 | 0.796 | 0.782 | 0.768 | 0.754 | 0.74 | 0.716 | 0.692 | 0.668 | 0.644 | 0.62 | 1.1561 | 42 | 1.1561 | 42
9.1 | 1.062 |  |  |  | 7.1 | 1.6513 | 1.5701 | 1.4888 | 1.4076 | 1.3264 | 1.2451 | 1.2279 | 1.2107 | 1.1935 | 1.1763 | 1.1591 | 1.1419 | 1.1247 | 1.1075 | 1.0604 | 1.0133 | 0.97367 | 0.934 | 0.89433 | 0.85467 | 0.815 | 0.8008 | 0.7866 | 0.7724 | 0.7582 | 0.744 | 0.71973 | 0.69547 | 0.6712 | 0.64693 | 0.62267 | 1.1591 | 43 | 1.1591 | 43
9.2 | 1.064 |  |  |  | 7.2 | 1.6586 | 1.5767 | 1.4948 | 1.4129 | 1.331 | 1.249 | 1.2317 | 1.2143 | 1.1969 | 1.1795 | 1.1621 | 1.1448 | 1.1274 | 1.11 | 1.0633 | 1.0167 | 0.97733 | 0.938 | 0.89867 | 0.85933 | 0.82 | 0.8056 | 0.7912 | 0.7768 | 0.7624 | 0.748 | 0.72347 | 0.69893 | 0.6744 | 0.64987 | 0.62533 | 1.1621 | 44 | 1.1621 | 44
9.3 | 1.066 |  |  |  | 7.3 | 1.6659 | 1.5833 | 1.5007 | 1.4182 | 1.3356 | 1.253 | 1.2354 | 1.2179 | 1.2003 | 1.1827 | 1.1652 | 1.1476 | 1.1301 | 1.1125 | 1.0662 | 1.02 | 0.981 | 0.942 | 0.903 | 0.864 | 0.825 | 0.8104 | 0.7958 | 0.7812 | 0.7666 | 0.752 | 0.7272 | 0.7024 | 0.6776 | 0.6528 | 0.628 | 1.1652 | 45 | 1.1652 | 45
9.4 | 1.068 |  |  |  | 7.4 | 1.6732 | 1.59 | 1.5067 | 1.4234 | 1.3402 | 1.2569 | 1.2392 | 1.2214 | 1.2037 | 1.1859 | 1.1682 | 1.1505 | 1.1327 | 1.115 | 1.0692 | 1.0233 | 0.98467 | 0.946 | 0.90733 | 0.86867 | 0.83 | 0.8152 | 0.8004 | 0.7856 | 0.7708 | 0.756 | 0.73093 | 0.70587 | 0.6808 | 0.65573 | 0.63067 | 1.1682 | 46 | 1.1682 | 46
9.5 | 1.07 |  |  |  | 7.5 | 1.6805 | 1.5966 | 1.5126 | 1.4287 | 1.3448 | 1.2608 | 1.2429 | 1.225 | 1.2071 | 1.1892 | 1.1712 | 1.1533 | 1.1354 | 1.1175 | 1.0721 | 1.0267 | 0.98833 | 0.95 | 0.91167 | 0.87333 | 0.835 | 0.82 | 0.805 | 0.79 | 0.775 | 0.76 | 0.73467 | 0.70933 | 0.684 | 0.65867 | 0.63333 | 1.1712 | 47 | 1.1712 | 47
9.6 | 1.072 |  |  |  | 7.6 | 1.6878 | 1.6032 | 1.5186 | 1.434 | 1.3494 | 1.2647 | 1.2466 | 1.2286 | 1.2105 | 1.1924 | 1.1743 | 1.1562 | 1.1381 | 1.12 | 1.075 | 1.03 | 0.992 | 0.954 | 0.916 | 0.878 | 0.84 | 0.8248 | 0.8096 | 0.7944 | 0.7792 | 0.764 | 0.7384 | 0.7128 | 0.6872 | 0.6616 | 0.636 | 1.1743 | 48 | 1.1743 | 48
9.7 | 1.074 |  |  |  | 7.7 | 1.6951 | 1.6099 | 1.5246 | 1.4393 | 1.354 | 1.2687 | 1.2504 | 1.2321 | 1.2139 | 1.1956 | 1.1773 | 1.159 | 1.1408 | 1.1225 | 1.0779 | 1.0333 | 0.99567 | 0.958 | 0.92033 | 0.88267 | 0.845 | 0.8296 | 0.8142 | 0.7988 | 0.7834 | 0.768 | 0.74213 | 0.71627 | 0.6904 | 0.66453 | 0.63867 | 1.1773 | 49 | 1.1773 | 49
9.8 | 1.076 |  |  |  | 7.8 | 1.7025 | 1.6165 | 1.5305 | 1.4445 | 1.3586 | 1.2726 | 1.2541 | 1.2357 | 1.2172 | 1.1988 | 1.1803 | 1.1619 | 1.1434 | 1.125 | 1.0808 | 1.0367 | 0.99933 | 0.962 | 0.92467 | 0.88733 | 0.85 | 0.8344 | 0.8188 | 0.8032 | 0.7876 | 0.772 | 0.74587 | 0.71973 | 0.6936 | 0.66747 | 0.64133 | 1.1803 | 50 | 1.1803 | 50
9.9 | 1.078 |  |  |  | 7.9 | 1.7098 | 1.6231 | 1.5365 | 1.4498 | 1.3632 | 1.2765 | 1.2579 | 1.2393 | 1.2206 | 1.202 | 1.1834 | 1.1648 | 1.1461 | 1.1275 | 1.0837 | 1.04 | 1.003 | 0.966 | 0.929 | 0.892 | 0.855 | 0.8392 | 0.8234 | 0.8076 | 0.7918 | 0.776 | 0.7496 | 0.7232 | 0.6968 | 0.6704 | 0.644 | 1.1834 | 51 | 1.1834 | 51
10 | 1.08 |  |  |  | 8 | 1.7171 | 1.6297 | 1.5424 | 1.4551 | 1.3678 | 1.2804 | 1.2616 | 1.2428 | 1.224 | 1.2052 | 1.1864 | 1.1676 | 1.1488 | 1.13 | 1.0867 | 1.0433 | 1.0067 | 0.97 | 0.93333 | 0.89667 | 0.86 | 0.844 | 0.828 | 0.812 | 0.796 | 0.78 | 0.75333 | 0.72667 | 0.7 | 0.67333 | 0.64667 | 1.1864 | 52 | 1.1864 | 52
10.1 | 1.082 |  |  |  | 8.1 | 1.7244 | 1.6364 | 1.5484 | 1.4604 | 1.3724 | 1.2844 | 1.2654 | 1.2464 | 1.2274 | 1.2084 | 1.1894 | 1.1705 | 1.1515 | 1.1325 | 1.0896 | 1.0467 | 1.0103 | 0.974 | 0.93767 | 0.90133 | 0.865 | 0.8488 | 0.8326 | 0.8164 | 0.8002 | 0.784 | 0.75707 | 0.73013 | 0.7032 | 0.67627 | 0.64933 | 1.1894 | 53 | 1.1894 | 53
10.2 | 1.084 |  |  |  | 8.2 | 1.7317 | 1.643 | 1.5543 | 1.4656 | 1.377 | 1.2883 | 1.2691 | 1.25 | 1.2308 | 1.2116 | 1.1925 | 1.1733 | 1.1542 | 1.135 | 1.0925 | 1.05 | 1.014 | 0.978 | 0.942 | 0.906 | 0.87 | 0.8536 | 0.8372 | 0.8208 | 0.8044 | 0.788 | 0.7608 | 0.7336 | 0.7064 | 0.6792 | 0.652 | 1.1925 | 54 | 1.1925 | 54
10.3 | 1.086 |  |  |  | 8.3 | 1.739 | 1.6496 | 1.5603 | 1.4709 | 1.3816 | 1.2922 | 1.2729 | 1.2535 | 1.2342 | 1.2149 | 1.1955 | 1.1762 | 1.1568 | 1.1375 | 1.0954 | 1.0533 | 1.0177 | 0.982 | 0.94633 | 0.91067 | 0.875 | 0.8584 | 0.8418 | 0.8252 | 0.8086 | 0.792 | 0.76453 | 0.73707 | 0.7096 | 0.68213 | 0.65467 | 1.1955 | 55 | 1.1955 | 55
10.4 | 1.088 |  |  |  | 8.4 | 1.7463 | 1.6563 | 1.5662 | 1.4762 | 1.3862 | 1.2961 | 1.2766 | 1.2571 | 1.2376 | 1.2181 | 1.1985 | 1.179 | 1.1595 | 1.14 | 1.0983 | 1.0567 | 1.0213 | 0.986 | 0.95067 | 0.91533 | 0.88 | 0.8632 | 0.8464 | 0.8296 | 0.8128 | 0.796 | 0.76827 | 0.74053 | 0.7128 | 0.68507 | 0.65733 | 1.1985 | 56 | 1.1985 | 56
10.5 | 1.09 |  |  |  | 8.5 | 1.7536 | 1.6629 | 1.5722 | 1.4815 | 1.3908 | 1.3 | 1.2804 | 1.2607 | 1.241 | 1.2213 | 1.2016 | 1.1819 | 1.1622 | 1.1425 | 1.1013 | 1.06 | 1.025 | 0.99 | 0.955 | 0.92 | 0.885 | 0.868 | 0.851 | 0.834 | 0.817 | 0.8 | 0.772 | 0.744 | 0.716 | 0.688 | 0.66 | 1.2016 | 57 | 1.2016 | 57
10.6 | 1.092 |  |  |  | 8.6 | 1.7609 | 1.6695 | 1.5781 | 1.4867 | 1.3954 | 1.304 | 1.2841 | 1.2642 | 1.2444 | 1.2245 | 1.2046 | 1.1847 | 1.1649 | 1.145 | 1.1042 | 1.0633 | 1.0287 | 0.994 | 0.95933 | 0.92467 | 0.89 | 0.8728 | 0.8556 | 0.8384 | 0.8212 | 0.804 | 0.77573 | 0.74747 | 0.7192 | 0.69093 | 0.66267 | 1.2046 | 58 | 1.2046 | 58
10.7 | 1.094 |  |  |  | 8.7 | 1.7682 | 1.6762 | 1.5841 | 1.492 | 1.4 | 1.3079 | 1.2878 | 1.2678 | 1.2477 | 1.2277 | 1.2076 | 1.1876 | 1.1675 | 1.1475 | 1.1071 | 1.0667 | 1.0323 | 0.998 | 0.96367 | 0.92933 | 0.895 | 0.8776 | 0.8602 | 0.8428 | 0.8254 | 0.808 | 0.77947 | 0.75093 | 0.7224 | 0.69387 | 0.66533 | 1.2076 | 59 | 1.2076 | 59
10.8 | 1.096 |  |  |  | 8.8 | 1.7755 | 1.6828 | 1.59 | 1.4973 | 1.4046 | 1.3118 | 1.2916 | 1.2714 | 1.2511 | 1.2309 | 1.2107 | 1.1905 | 1.1702 | 1.15 | 1.11 | 1.07 | 1.036 | 1.002 | 0.968 | 0.934 | 0.9 | 0.8824 | 0.8648 | 0.8472 | 0.8296 | 0.812 | 0.7832 | 0.7544 | 0.7256 | 0.6968 | 0.668 | 1.2107 | 60 | 1.2107 | 60
10.9 | 1.098 |  |  |  | 8.9 | 1.7828 | 1.6894 | 1.596 | 1.5026 | 1.4092 | 1.3157 | 1.2953 | 1.2749 | 1.2545 | 1.2341 | 1.2137 | 1.1933 | 1.1729 | 1.1525 | 1.1129 | 1.0733 | 1.0397 | 1.006 | 0.97233 | 0.93867 | 0.905 | 0.8872 | 0.8694 | 0.8516 | 0.8338 | 0.816 | 0.78693 | 0.75787 | 0.7288 | 0.69973 | 0.67067 | 1.2137 | 61 | 1.2137 | 61
11 | 1.1 |  |  |  | 9 | 1.7901 | 1.696 | 1.6019 | 1.5079 | 1.4138 | 1.3197 | 1.2991 | 1.2785 | 1.2579 | 1.2373 | 1.2167 | 1.1962 | 1.1756 | 1.155 | 1.1158 | 1.0767 | 1.0433 | 1.01 | 0.97667 | 0.94333 | 0.91 | 0.892 | 0.874 | 0.856 | 0.838 | 0.82 | 0.79067 | 0.76133 | 0.732 | 0.70267 | 0.67333 | 1.2167 | 62 | 1.2167 | 62
11.1 | 1.102 |  |  |  | 9.1 | 1.7974 | 1.7027 | 1.6079 | 1.5131 | 1.4184 | 1.3236 | 1.3028 | 1.2821 | 1.2613 | 1.2405 | 1.2198 | 1.199 | 1.1783 | 1.1575 | 1.1187 | 1.08 | 1.047 | 1.014 | 0.981 | 0.948 | 0.915 | 0.8968 | 0.8786 | 0.8604 | 0.8422 | 0.824 | 0.7944 | 0.7648 | 0.7352 | 0.7056 | 0.676 | 1.2198 | 63 | 1.2198 | 63
11.2 | 1.104 |  |  |  | 9.2 | 1.8047 | 1.7093 | 1.6139 | 1.5184 | 1.423 | 1.3275 | 1.3066 | 1.2856 | 1.2647 | 1.2438 | 1.2228 | 1.2019 | 1.1809 | 1.16 | 1.1217 | 1.0833 | 1.0507 | 1.018 | 0.98533 | 0.95267 | 0.92 | 0.9016 | 0.8832 | 0.8648 | 0.8464 | 0.828 | 0.79813 | 0.76827 | 0.7384 | 0.70853 | 0.67867 | 1.2228 | 64 | 1.2228 | 64
11.3 | 1.106 |  |  |  | 9.3 | 1.8121 | 1.7159 | 1.6198 | 1.5237 | 1.4276 | 1.3314 | 1.3103 | 1.2892 | 1.2681 | 1.247 | 1.2259 | 1.2047 | 1.1836 | 1.1625 | 1.1246 | 1.0867 | 1.0543 | 1.022 | 0.98967 | 0.95733 | 0.925 | 0.9064 | 0.8878 | 0.8692 | 0.8506 | 0.832 | 0.80187 | 0.77173 | 0.7416 | 0.71147 | 0.68133 | 1.2259 | 65 | 1.2259 | 65
11.4 | 1.108 |  |  |  | 9.4 | 1.8194 | 1.7226 | 1.6258 | 1.529 | 1.4322 | 1.3354 | 1.3141 | 1.2928 | 1.2715 | 1.2502 | 1.2289 | 1.2076 | 1.1863 | 1.165 | 1.1275 | 1.09 | 1.058 | 1.026 | 0.994 | 0.962 | 0.93 | 0.9112 | 0.8924 | 0.8736 | 0.8548 | 0.836 | 0.8056 | 0.7752 | 0.7448 | 0.7144 | 0.684 | 1.2289 | 66 | 1.2289 | 66
11.5 | 1.11 |  |  |  | 9.5 | 1.8267 | 1.7292 | 1.6317 | 1.5342 | 1.4368 | 1.3393 | 1.3178 | 1.2963 | 1.2749 | 1.2534 | 1.2319 | 1.2104 | 1.189 | 1.1675 | 1.1304 | 1.0933 | 1.0617 | 1.03 | 0.99833 | 0.96667 | 0.935 | 0.916 | 0.897 | 0.878 | 0.859 | 0.84 | 0.80933 | 0.77867 | 0.748 | 0.71733 | 0.68667 | 1.2319 | 67 | 1.2319 | 67
11.6 | 1.112 |  |  |  | 9.6 | 1.834 | 1.7358 | 1.6377 | 1.5395 | 1.4414 | 1.3432 | 1.3216 | 1.2999 | 1.2783 | 1.2566 | 1.235 | 1.2133 | 1.1917 | 1.17 | 1.1333 | 1.0967 | 1.0653 | 1.034 | 1.0027 | 0.97133 | 0.94 | 0.9208 | 0.9016 | 0.8824 | 0.8632 | 0.844 | 0.81307 | 0.78213 | 0.7512 | 0.72027 | 0.68933 | 1.235 | 68 | 1.235 | 68
11.7 | 1.114 |  |  |  | 9.7 | 1.8413 | 1.7425 | 1.6436 | 1.5448 | 1.446 | 1.3471 | 1.3253 | 1.3035 | 1.2816 | 1.2598 | 1.238 | 1.2162 | 1.1943 | 1.1725 | 1.1362 | 1.1 | 1.069 | 1.038 | 1.007 | 0.976 | 0.945 | 0.9256 | 0.9062 | 0.8868 | 0.8674 | 0.848 | 0.8168 | 0.7856 | 0.7544 | 0.7232 | 0.692 | 1.238 | 69 | 1.238 | 69
11.8 | 1.116 |  |  |  | 9.8 | 1.8486 | 1.7491 | 1.6496 | 1.5501 | 1.4506 | 1.3511 | 1.329 | 1.307 | 1.285 | 1.263 | 1.241 | 1.219 | 1.197 | 1.175 | 1.1392 | 1.1033 | 1.0727 | 1.042 | 1.0113 | 0.98067 | 0.95 | 0.9304 | 0.9108 | 0.8912 | 0.8716 | 0.852 | 0.82053 | 0.78907 | 0.7576 | 0.72613 | 0.69467 | 1.241 | 70 | 1.241 | 70
11.9 | 1.118 |  |  |  | 9.9 | 1.8559 | 1.7557 | 1.6555 | 1.5553 | 1.4552 | 1.355 | 1.3328 | 1.3106 | 1.2884 | 1.2662 | 1.2441 | 1.2219 | 1.1997 | 1.1775 | 1.1421 | 1.1067 | 1.0763 | 1.046 | 1.0157 | 0.98533 | 0.955 | 0.9352 | 0.9154 | 0.8956 | 0.8758 | 0.856 | 0.82427 | 0.79253 | 0.7608 | 0.72907 | 0.69733 | 1.2441 | 71 | 1.2441 | 71
12 | 1.12 |  |  |  | 10 | 1.8632 | 1.7623 | 1.6615 | 1.5606 | 1.4598 | 1.3589 | 1.3365 | 1.3142 | 1.2918 | 1.2694 | 1.2471 | 1.2247 | 1.2024 | 1.18 | 1.145 | 1.11 | 1.08 | 1.05 | 1.02 | 0.99 | 0.96 | 0.94 | 0.92 | 0.9 | 0.88 | 0.86 | 0.828 | 0.796 | 0.764 | 0.732 | 0.7 | 1.2471 | 72 | 1.2471 | 72
12.1 | 1.121
12.2 | 1.122
12.3 | 1.123 | [35 empty] | Max | 1.2471 | Max | 1.2471
12.4 | 1.124 | [35 empty] | Min | 0.93875 | Min | 0.93875
12.5 | 1.125
12.6 | 1.126
12.7 | 1.127
12.8 | 1.128
12.9 | 1.129
13 | 1.13
13.1 | 1.132
13.2 | 1.134
13.3 | 1.136
13.4 | 1.138
13.5 | 1.14
13.6 | 1.142
13.7 | 1.144
13.8 | 1.146
13.9 | 1.148
14 | 1.15
14.1 | 1.151
14.2 | 1.152
14.3 | 1.153
14.4 | 1.154
14.5 | 1.155
14.6 | 1.156
14.7 | 1.157
14.8 | 1.158
14.9 | 1.159
15 | 1.16
15.1 | 1.161
15.2 | 1.162
15.3 | 1.163
15.4 | 1.164
15.5 | 1.165
15.6 | 1.166
15.7 | 1.167
15.8 | 1.168
15.9 | 1.169
16 | 1.17
Ambient Vs PDP
Ambient Temp (°C) | RH = 26% | Row number for water content
10 | -8 | 65
12 | -6 | 67
14 | -5 | 68
16 | -3 | 70
18 | -2 | 71
20 | 0 | 73
22 | 1 | 74
24 | 3 | 76
26 | 4 | 77
28 | 6 | 79
30 | 8 | 81
32 | 9 | 82
34 | 11 | 84
36 | 13 | 86
38 | 14 | 87
40 | 16 | 89
42 | 18 | 91
44 | 19 | 92
46 | 21 | 94
48 | 23 | 96
50 | 24 | 97
52 | 26 | 99
54 | 28 | 101
56 | 29 | 102

## Correction Factors60HZ (hidden)
Pressure Correction |  |  | Ambient Correction |  | PDP Inlet Correction
Inlet pressure | Correction factor |  | Ambient temperature | Correction factor |  | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | Relevant Column |  | Relevant Column
5 | 0.9 |  | 25 | 1 | 3 | 1.37 | 1.31 | 1.25 | 1.19 | 1.13 | 1.07 | 1.0437 | 1.0175 | 0.99125 | 0.965 | 0.93875 | 0.9125 | 0.88625 | 0.86 | 0.83 | 0.8 | 0.77 | 0.74 | 0.71 | 0.68 | 0.65 | 0.63 | 0.61 | 0.59 | 0.57 | 0.55 | 0.528 | 0.506 | 0.484 | 0.462 | 0.44 | 0.93875 | 2 | 0.93875 | 2
5.1 | 0.906 |  | 26 | 1 | 3.1 | 1.38 | 1.3197 | 1.2594 | 1.1991 | 1.1388 | 1.0785 | 1.0529 | 1.0274 | 1.0018 | 0.97625 | 0.95069 | 0.92512 | 0.89956 | 0.874 | 0.8375 | 0.801 | 0.7712 | 0.7414 | 0.7116 | 0.6818 | 0.652 | 0.6321 | 0.6122 | 0.5923 | 0.5724 | 0.5525 | 0.5305 | 0.5085 | 0.4865 | 0.4645 | 0.4425 | 0.95069 | 3 | 0.95069 | 3
5.2 | 0.912 |  | 27 | 1 | 3.2 | 1.39 | 1.3294 | 1.2688 | 1.2082 | 1.1476 | 1.087 | 1.0621 | 1.0373 | 1.0124 | 0.9875 | 0.96262 | 0.93775 | 0.91287 | 0.888 | 0.845 | 0.802 | 0.7724 | 0.7428 | 0.7132 | 0.6836 | 0.654 | 0.6342 | 0.6144 | 0.5946 | 0.5748 | 0.555 | 0.533 | 0.511 | 0.489 | 0.467 | 0.445 | 0.96262 | 4 | 0.96262 | 4
5.3 | 0.918 |  | 28 | 1 | 3.3 | 1.4 | 1.3391 | 1.2782 | 1.2173 | 1.1564 | 1.0955 | 1.0713 | 1.0471 | 1.0229 | 0.99875 | 0.97456 | 0.95037 | 0.92619 | 0.902 | 0.8525 | 0.803 | 0.7736 | 0.7442 | 0.7148 | 0.6854 | 0.656 | 0.6363 | 0.6166 | 0.5969 | 0.5772 | 0.5575 | 0.5355 | 0.5135 | 0.4915 | 0.4695 | 0.4475 | 0.97456 | 5 | 0.97456 | 5
5.4 | 0.924 |  | 29 | 1 | 3.4 | 1.41 | 1.3488 | 1.2876 | 1.2264 | 1.1652 | 1.104 | 1.0805 | 1.057 | 1.0335 | 1.01 | 0.9865 | 0.963 | 0.9395 | 0.916 | 0.86 | 0.804 | 0.7748 | 0.7456 | 0.7164 | 0.6872 | 0.658 | 0.6384 | 0.6188 | 0.5992 | 0.5796 | 0.56 | 0.538 | 0.516 | 0.494 | 0.472 | 0.45 | 0.9865 | 6 | 0.9865 | 6
5.5 | 0.93 |  | 30 | 1 | 3.5 | 1.42 | 1.3585 | 1.297 | 1.2355 | 1.174 | 1.1125 | 1.0897 | 1.0669 | 1.0441 | 1.0212 | 0.99844 | 0.97562 | 0.95281 | 0.93 | 0.8675 | 0.805 | 0.776 | 0.747 | 0.718 | 0.689 | 0.66 | 0.6405 | 0.621 | 0.6015 | 0.582 | 0.5625 | 0.5405 | 0.5185 | 0.4965 | 0.4745 | 0.4525 | 0.99844 | 7 | 0.99844 | 7
5.6 | 0.936 |  | 31 | 1 | 3.6 | 1.43 | 1.3682 | 1.3064 | 1.2446 | 1.1828 | 1.121 | 1.0989 | 1.0768 | 1.0546 | 1.0325 | 1.0104 | 0.98825 | 0.96613 | 0.944 | 0.875 | 0.806 | 0.7772 | 0.7484 | 0.7196 | 0.6908 | 0.662 | 0.6426 | 0.6232 | 0.6038 | 0.5844 | 0.565 | 0.543 | 0.521 | 0.499 | 0.477 | 0.455 | 1.0104 | 8 | 1.0104 | 8
5.7 | 0.942 |  | 32 | 1 | 3.7 | 1.44 | 1.3779 | 1.3158 | 1.2537 | 1.1916 | 1.1295 | 1.1081 | 1.0866 | 1.0652 | 1.0437 | 1.0223 | 1.0009 | 0.97944 | 0.958 | 0.8825 | 0.807 | 0.7784 | 0.7498 | 0.7212 | 0.6926 | 0.664 | 0.6447 | 0.6254 | 0.6061 | 0.5868 | 0.5675 | 0.5455 | 0.5235 | 0.5015 | 0.4795 | 0.4575 | 1.0223 | 9 | 1.0223 | 9
5.8 | 0.948 |  | 33 | 1 | 3.8 | 1.45 | 1.3876 | 1.3252 | 1.2628 | 1.2004 | 1.138 | 1.1173 | 1.0965 | 1.0757 | 1.055 | 1.0342 | 1.0135 | 0.99275 | 0.972 | 0.89 | 0.808 | 0.7796 | 0.7512 | 0.7228 | 0.6944 | 0.666 | 0.6468 | 0.6276 | 0.6084 | 0.5892 | 0.57 | 0.548 | 0.526 | 0.504 | 0.482 | 0.46 | 1.0342 | 10 | 1.0342 | 10
5.9 | 0.954 |  | 34 | 1 | 3.9 | 1.46 | 1.3973 | 1.3346 | 1.2719 | 1.2092 | 1.1465 | 1.1264 | 1.1064 | 1.0863 | 1.0662 | 1.0462 | 1.0261 | 1.0061 | 0.986 | 0.8975 | 0.809 | 0.7808 | 0.7526 | 0.7244 | 0.6962 | 0.668 | 0.6489 | 0.6298 | 0.6107 | 0.5916 | 0.5725 | 0.5505 | 0.5285 | 0.5065 | 0.4845 | 0.4625 | 1.0462 | 11 | 1.0462 | 11
6 | 0.96 |  | 35 | 1 | 4 | 1.47 | 1.424 | 1.378 | 1.332 | 1.286 | 1.24 | 1.21 | 1.18 | 1.15 | 1.12 | 1.09 | 1.06 | 1.03 | 1 | 0.91 | 0.82 | 0.794 | 0.768 | 0.742 | 0.716 | 0.69 | 0.667 | 0.644 | 0.621 | 0.598 | 0.575 | 0.553 | 0.531 | 0.509 | 0.487 | 0.465 | 1.09 | 12 | 1.09 | 12
6.1 | 0.964 |  | 36 | 1 | 4.1 | 1.48 | 1.4337 | 1.3874 | 1.3411 | 1.2948 | 1.2485 | 1.2193 | 1.1901 | 1.1609 | 1.1318 | 1.1026 | 1.0734 | 1.0442 | 1.015 | 0.918 | 0.821 | 0.7952 | 0.7694 | 0.7436 | 0.7178 | 0.692 | 0.6691 | 0.6462 | 0.6233 | 0.6004 | 0.5775 | 0.5555 | 0.5335 | 0.5115 | 0.4895 | 0.4675 | 1.1026 | 13 | 1.1026 | 13
6.2 | 0.968 |  | 37 | 1 | 4.2 | 1.49 | 1.4434 | 1.3968 | 1.3502 | 1.3036 | 1.257 | 1.2286 | 1.2003 | 1.1719 | 1.1435 | 1.1151 | 1.0868 | 1.0584 | 1.03 | 0.926 | 0.822 | 0.7964 | 0.7708 | 0.7452 | 0.7196 | 0.694 | 0.6712 | 0.6484 | 0.6256 | 0.6028 | 0.58 | 0.558 | 0.536 | 0.514 | 0.492 | 0.47 | 1.1151 | 14 | 1.1151 | 14
6.3 | 0.972 |  | 38 | 1 | 4.3 | 1.5 | 1.4531 | 1.4062 | 1.3593 | 1.3124 | 1.2655 | 1.2379 | 1.2104 | 1.1828 | 1.1553 | 1.1277 | 1.1001 | 1.0726 | 1.045 | 0.934 | 0.823 | 0.7976 | 0.7722 | 0.7468 | 0.7214 | 0.696 | 0.6733 | 0.6506 | 0.6279 | 0.6052 | 0.5825 | 0.5605 | 0.5385 | 0.5165 | 0.4945 | 0.4725 | 1.1277 | 15 | 1.1277 | 15
6.4 | 0.976 |  | 39 | 0.96 | 4.4 | 1.51 | 1.4628 | 1.4156 | 1.3684 | 1.3212 | 1.274 | 1.2472 | 1.2205 | 1.1938 | 1.167 | 1.1402 | 1.1135 | 1.0868 | 1.06 | 0.942 | 0.824 | 0.7988 | 0.7736 | 0.7484 | 0.7232 | 0.698 | 0.6754 | 0.6528 | 0.6302 | 0.6076 | 0.585 | 0.563 | 0.541 | 0.519 | 0.497 | 0.475 | 1.1402 | 16 | 1.1402 | 16
6.5 | 0.98 |  | 40 | 0.8 | 4.5 | 1.52 | 1.4725 | 1.425 | 1.3775 | 1.33 | 1.2825 | 1.2566 | 1.2306 | 1.2047 | 1.1787 | 1.1528 | 1.1269 | 1.1009 | 1.075 | 0.95 | 0.825 | 0.8 | 0.775 | 0.75 | 0.725 | 0.7 | 0.6775 | 0.655 | 0.6325 | 0.61 | 0.5875 | 0.5655 | 0.5435 | 0.5215 | 0.4995 | 0.4775 | 1.1528 | 17 | 1.1528 | 17
6.6 | 0.984 |  | 41 | 0.788 | 4.6 | 1.53 | 1.4822 | 1.4344 | 1.3866 | 1.3388 | 1.291 | 1.2659 | 1.2408 | 1.2156 | 1.1905 | 1.1654 | 1.1402 | 1.1151 | 1.09 | 0.958 | 0.826 | 0.8012 | 0.7764 | 0.7516 | 0.7268 | 0.702 | 0.6796 | 0.6572 | 0.6348 | 0.6124 | 0.59 | 0.568 | 0.546 | 0.524 | 0.502 | 0.48 | 1.1654 | 18 | 1.1654 | 18
6.7 | 0.988 |  | 42 | 0.776 | 4.7 | 1.54 | 1.4919 | 1.4438 | 1.3957 | 1.3476 | 1.2995 | 1.2752 | 1.2509 | 1.2266 | 1.2023 | 1.1779 | 1.1536 | 1.1293 | 1.105 | 0.966 | 0.827 | 0.8024 | 0.7778 | 0.7532 | 0.7286 | 0.704 | 0.6817 | 0.6594 | 0.6371 | 0.6148 | 0.5925 | 0.5705 | 0.5485 | 0.5265 | 0.5045 | 0.4825 | 1.1779 | 19 | 1.1779 | 19
6.8 | 0.992 |  | 43 | 0.764 | 4.8 | 1.55 | 1.5016 | 1.4532 | 1.4048 | 1.3564 | 1.308 | 1.2845 | 1.261 | 1.2375 | 1.214 | 1.1905 | 1.167 | 1.1435 | 1.12 | 0.974 | 0.828 | 0.8036 | 0.7792 | 0.7548 | 0.7304 | 0.706 | 0.6838 | 0.6616 | 0.6394 | 0.6172 | 0.595 | 0.573 | 0.551 | 0.529 | 0.507 | 0.485 | 1.1905 | 20 | 1.1905 | 20
6.9 | 0.996 |  | 44 | 0.752 | 4.9 | 1.56 | 1.5113 | 1.4626 | 1.4139 | 1.3652 | 1.3165 | 1.2938 | 1.2711 | 1.2484 | 1.2257 | 1.2031 | 1.1804 | 1.1577 | 1.135 | 0.982 | 0.829 | 0.8048 | 0.7806 | 0.7564 | 0.7322 | 0.708 | 0.6859 | 0.6638 | 0.6417 | 0.6196 | 0.5975 | 0.5755 | 0.5535 | 0.5315 | 0.5095 | 0.4875 | 1.2031 | 21 | 1.2031 | 21
7 | 1 |  | 45 | 0.74 | 5 | 1.57 | 1.504 | 1.438 | 1.372 | 1.306 | 1.24 | 1.2288 | 1.2175 | 1.2063 | 1.195 | 1.1838 | 1.1725 | 1.1612 | 1.15 | 0.985 | 0.82 | 0.794 | 0.768 | 0.742 | 0.716 | 0.69 | 0.672 | 0.654 | 0.636 | 0.618 | 0.6 | 0.578 | 0.556 | 0.534 | 0.512 | 0.49 | 1.1838 | 22 | 1.1838 | 22
7.1 | 1.003 |  |  |  | 5.1 | 1.5737 | 1.507 | 1.4402 | 1.3735 | 1.3068 | 1.2401 | 1.2285 | 1.217 | 1.2054 | 1.1939 | 1.1824 | 1.1708 | 1.1593 | 1.1478 | 0.98862 | 0.8295 | 0.8028 | 0.7761 | 0.7494 | 0.7227 | 0.696 | 0.6782 | 0.6604 | 0.6426 | 0.6248 | 0.607 | 0.5849 | 0.5628 | 0.5407 | 0.5186 | 0.4965 | 1.1824 | 23 | 1.1824 | 23
7.2 | 1.006 |  |  |  | 5.2 | 1.5774 | 1.5099 | 1.4425 | 1.375 | 1.3076 | 1.2401 | 1.2283 | 1.2165 | 1.2046 | 1.1928 | 1.181 | 1.1692 | 1.1573 | 1.1455 | 0.99225 | 0.839 | 0.8116 | 0.7842 | 0.7568 | 0.7294 | 0.702 | 0.6844 | 0.6668 | 0.6492 | 0.6316 | 0.614 | 0.5918 | 0.5696 | 0.5474 | 0.5252 | 0.503 | 1.181 | 24 | 1.181 | 24
7.3 | 1.009 |  |  |  | 5.3 | 1.5811 | 1.5129 | 1.4447 | 1.3765 | 1.3084 | 1.2402 | 1.2281 | 1.2159 | 1.2038 | 1.1917 | 1.1796 | 1.1675 | 1.1554 | 1.1433 | 0.99587 | 0.8485 | 0.8204 | 0.7923 | 0.7642 | 0.7361 | 0.708 | 0.6906 | 0.6732 | 0.6558 | 0.6384 | 0.621 | 0.5987 | 0.5764 | 0.5541 | 0.5318 | 0.5095 | 1.1796 | 25 | 1.1796 | 25
7.4 | 1.012 |  |  |  | 5.4 | 1.5848 | 1.5159 | 1.447 | 1.3781 | 1.3092 | 1.2402 | 1.2278 | 1.2154 | 1.203 | 1.1906 | 1.1782 | 1.1658 | 1.1534 | 1.141 | 0.9995 | 0.858 | 0.8292 | 0.8004 | 0.7716 | 0.7428 | 0.714 | 0.6968 | 0.6796 | 0.6624 | 0.6452 | 0.628 | 0.6056 | 0.5832 | 0.5608 | 0.5384 | 0.516 | 1.1782 | 26 | 1.1782 | 26
7.5 | 1.015 |  |  |  | 5.5 | 1.5885 | 1.5189 | 1.4492 | 1.3796 | 1.3099 | 1.2403 | 1.2276 | 1.2149 | 1.2022 | 1.1895 | 1.1768 | 1.1641 | 1.1514 | 1.1387 | 1.0031 | 0.8675 | 0.838 | 0.8085 | 0.779 | 0.7495 | 0.72 | 0.703 | 0.686 | 0.669 | 0.652 | 0.635 | 0.6125 | 0.59 | 0.5675 | 0.545 | 0.5225 | 1.1768 | 27 | 1.1768 | 27
7.6 | 1.018 |  |  |  | 5.6 | 1.5922 | 1.5218 | 1.4515 | 1.3811 | 1.3107 | 1.2404 | 1.2274 | 1.2144 | 1.2014 | 1.1884 | 1.1754 | 1.1625 | 1.1495 | 1.1365 | 1.0068 | 0.877 | 0.8468 | 0.8166 | 0.7864 | 0.7562 | 0.726 | 0.7092 | 0.6924 | 0.6756 | 0.6588 | 0.642 | 0.6194 | 0.5968 | 0.5742 | 0.5516 | 0.529 | 1.1754 | 28 | 1.1754 | 28
7.7 | 1.021 |  |  |  | 5.7 | 1.5959 | 1.5248 | 1.4537 | 1.3826 | 1.3115 | 1.2404 | 1.2271 | 1.2139 | 1.2006 | 1.1873 | 1.1741 | 1.1608 | 1.1475 | 1.1342 | 1.0104 | 0.8865 | 0.8556 | 0.8247 | 0.7938 | 0.7629 | 0.732 | 0.7154 | 0.6988 | 0.6822 | 0.6656 | 0.649 | 0.6263 | 0.6036 | 0.5809 | 0.5582 | 0.5355 | 1.1741 | 29 | 1.1741 | 29
7.8 | 1.024 |  |  |  | 5.8 | 1.5996 | 1.5278 | 1.456 | 1.3841 | 1.3123 | 1.2405 | 1.2269 | 1.2134 | 1.1998 | 1.1862 | 1.1727 | 1.1591 | 1.1456 | 1.132 | 1.014 | 0.896 | 0.8644 | 0.8328 | 0.8012 | 0.7696 | 0.738 | 0.7216 | 0.7052 | 0.6888 | 0.6724 | 0.656 | 0.6332 | 0.6104 | 0.5876 | 0.5648 | 0.542 | 1.1727 | 30 | 1.1727 | 30
7.9 | 1.027 |  |  |  | 5.9 | 1.6033 | 1.5307 | 1.4582 | 1.3856 | 1.3131 | 1.2405 | 1.2267 | 1.2128 | 1.199 | 1.1851 | 1.1713 | 1.1574 | 1.1436 | 1.1298 | 1.0176 | 0.9055 | 0.8732 | 0.8409 | 0.8086 | 0.7763 | 0.744 | 0.7278 | 0.7116 | 0.6954 | 0.6792 | 0.663 | 0.6401 | 0.6172 | 0.5943 | 0.5714 | 0.5485 | 1.1713 | 31 | 1.1713 | 31
8 | 1.03 |  |  |  | 6 | 1.607 | 1.5337 | 1.4604 | 1.3872 | 1.3139 | 1.2406 | 1.2265 | 1.2123 | 1.1982 | 1.1841 | 1.1699 | 1.1558 | 1.1416 | 1.1275 | 1.0212 | 0.915 | 0.882 | 0.849 | 0.816 | 0.783 | 0.75 | 0.734 | 0.718 | 0.702 | 0.686 | 0.67 | 0.647 | 0.624 | 0.601 | 0.578 | 0.555 | 1.1699 | 32 | 1.1699 | 32
8.1 | 1.033 |  |  |  | 6.1 | 1.6107 | 1.5367 | 1.4627 | 1.3887 | 1.3147 | 1.2407 | 1.2262 | 1.2118 | 1.1974 | 1.183 | 1.1685 | 1.1541 | 1.1397 | 1.1253 | 1.0249 | 0.9245 | 0.8908 | 0.8571 | 0.8234 | 0.7897 | 0.756 | 0.7402 | 0.7244 | 0.7086 | 0.6928 | 0.677 | 0.6539 | 0.6308 | 0.6077 | 0.5846 | 0.5615 | 1.1685 | 33 | 1.1685 | 33
8.2 | 1.036 |  |  |  | 6.2 | 1.6144 | 1.5397 | 1.4649 | 1.3902 | 1.3155 | 1.2407 | 1.226 | 1.2113 | 1.1966 | 1.1819 | 1.1671 | 1.1524 | 1.1377 | 1.123 | 1.0285 | 0.934 | 0.8996 | 0.8652 | 0.8308 | 0.7964 | 0.762 | 0.7464 | 0.7308 | 0.7152 | 0.6996 | 0.684 | 0.6608 | 0.6376 | 0.6144 | 0.5912 | 0.568 | 1.1671 | 34 | 1.1671 | 34
8.3 | 1.039 |  |  |  | 6.3 | 1.6181 | 1.5426 | 1.4672 | 1.3917 | 1.3162 | 1.2408 | 1.2258 | 1.2108 | 1.1958 | 1.1808 | 1.1658 | 1.1508 | 1.1358 | 1.1207 | 1.0321 | 0.9435 | 0.9084 | 0.8733 | 0.8382 | 0.8031 | 0.768 | 0.7526 | 0.7372 | 0.7218 | 0.7064 | 0.691 | 0.6677 | 0.6444 | 0.6211 | 0.5978 | 0.5745 | 1.1658 | 35 | 1.1658 | 35
8.4 | 1.042 |  |  |  | 6.4 | 1.6218 | 1.5456 | 1.4694 | 1.3932 | 1.317 | 1.2408 | 1.2255 | 1.2103 | 1.195 | 1.1797 | 1.1644 | 1.1491 | 1.1338 | 1.1185 | 1.0357 | 0.953 | 0.9172 | 0.8814 | 0.8456 | 0.8098 | 0.774 | 0.7588 | 0.7436 | 0.7284 | 0.7132 | 0.698 | 0.6746 | 0.6512 | 0.6278 | 0.6044 | 0.581 | 1.1644 | 36 | 1.1644 | 36
8.5 | 1.045 |  |  |  | 6.5 | 1.6255 | 1.5486 | 1.4717 | 1.3947 | 1.3178 | 1.2409 | 1.2253 | 1.2097 | 1.1942 | 1.1786 | 1.163 | 1.1474 | 1.1318 | 1.1162 | 1.0394 | 0.9625 | 0.926 | 0.8895 | 0.853 | 0.8165 | 0.78 | 0.765 | 0.75 | 0.735 | 0.72 | 0.705 | 0.6815 | 0.658 | 0.6345 | 0.611 | 0.5875 | 1.163 | 37 | 1.163 | 37
8.6 | 1.048 |  |  |  | 6.6 | 1.6292 | 1.5516 | 1.4739 | 1.3963 | 1.3186 | 1.241 | 1.2251 | 1.2092 | 1.1933 | 1.1775 | 1.1616 | 1.1457 | 1.1299 | 1.114 | 1.043 | 0.972 | 0.9348 | 0.8976 | 0.8604 | 0.8232 | 0.786 | 0.7712 | 0.7564 | 0.7416 | 0.7268 | 0.712 | 0.6884 | 0.6648 | 0.6412 | 0.6176 | 0.594 | 1.1616 | 38 | 1.1616 | 38
8.7 | 1.051 |  |  |  | 6.7 | 1.6329 | 1.5545 | 1.4761 | 1.3978 | 1.3194 | 1.241 | 1.2249 | 1.2087 | 1.1925 | 1.1764 | 1.1602 | 1.1441 | 1.1279 | 1.1118 | 1.0466 | 0.9815 | 0.9436 | 0.9057 | 0.8678 | 0.8299 | 0.792 | 0.7774 | 0.7628 | 0.7482 | 0.7336 | 0.719 | 0.6953 | 0.6716 | 0.6479 | 0.6242 | 0.6005 | 1.1602 | 39 | 1.1602 | 39
8.8 | 1.054 |  |  |  | 6.8 | 1.6366 | 1.5575 | 1.4784 | 1.3993 | 1.3202 | 1.2411 | 1.2246 | 1.2082 | 1.1917 | 1.1753 | 1.1588 | 1.1424 | 1.1259 | 1.1095 | 1.0502 | 0.991 | 0.9524 | 0.9138 | 0.8752 | 0.8366 | 0.798 | 0.7836 | 0.7692 | 0.7548 | 0.7404 | 0.726 | 0.7022 | 0.6784 | 0.6546 | 0.6308 | 0.607 | 1.1588 | 40 | 1.1588 | 40
8.9 | 1.057 |  |  |  | 6.9 | 1.6403 | 1.5605 | 1.4806 | 1.4008 | 1.321 | 1.2411 | 1.2244 | 1.2077 | 1.1909 | 1.1742 | 1.1575 | 1.1407 | 1.124 | 1.1073 | 1.0539 | 1.0005 | 0.9612 | 0.9219 | 0.8826 | 0.8433 | 0.804 | 0.7898 | 0.7756 | 0.7614 | 0.7472 | 0.733 | 0.7091 | 0.6852 | 0.6613 | 0.6374 | 0.6135 | 1.1575 | 41 | 1.1575 | 41
9 | 1.06 |  |  |  | 7 | 1.644 | 1.5634 | 1.4829 | 1.4023 | 1.3218 | 1.2412 | 1.2242 | 1.2071 | 1.1901 | 1.1731 | 1.1561 | 1.139 | 1.122 | 1.105 | 1.0575 | 1.01 | 0.97 | 0.93 | 0.89 | 0.85 | 0.81 | 0.796 | 0.782 | 0.768 | 0.754 | 0.74 | 0.716 | 0.692 | 0.668 | 0.644 | 0.62 | 1.1561 | 42 | 1.1561 | 42
9.1 | 1.062 |  |  |  | 7.1 | 1.6513 | 1.5701 | 1.4888 | 1.4076 | 1.3264 | 1.2451 | 1.2279 | 1.2107 | 1.1935 | 1.1763 | 1.1591 | 1.1419 | 1.1247 | 1.1075 | 1.0604 | 1.0133 | 0.97367 | 0.934 | 0.89433 | 0.85467 | 0.815 | 0.8008 | 0.7866 | 0.7724 | 0.7582 | 0.744 | 0.71973 | 0.69547 | 0.6712 | 0.64693 | 0.62267 | 1.1591 | 43 | 1.1591 | 43
9.2 | 1.064 |  |  |  | 7.2 | 1.6586 | 1.5767 | 1.4948 | 1.4129 | 1.331 | 1.249 | 1.2317 | 1.2143 | 1.1969 | 1.1795 | 1.1621 | 1.1448 | 1.1274 | 1.11 | 1.0633 | 1.0167 | 0.97733 | 0.938 | 0.89867 | 0.85933 | 0.82 | 0.8056 | 0.7912 | 0.7768 | 0.7624 | 0.748 | 0.72347 | 0.69893 | 0.6744 | 0.64987 | 0.62533 | 1.1621 | 44 | 1.1621 | 44
9.3 | 1.066 |  |  |  | 7.3 | 1.6659 | 1.5833 | 1.5007 | 1.4182 | 1.3356 | 1.253 | 1.2354 | 1.2179 | 1.2003 | 1.1827 | 1.1652 | 1.1476 | 1.1301 | 1.1125 | 1.0662 | 1.02 | 0.981 | 0.942 | 0.903 | 0.864 | 0.825 | 0.8104 | 0.7958 | 0.7812 | 0.7666 | 0.752 | 0.7272 | 0.7024 | 0.6776 | 0.6528 | 0.628 | 1.1652 | 45 | 1.1652 | 45
9.4 | 1.068 |  |  |  | 7.4 | 1.6732 | 1.59 | 1.5067 | 1.4234 | 1.3402 | 1.2569 | 1.2392 | 1.2214 | 1.2037 | 1.1859 | 1.1682 | 1.1505 | 1.1327 | 1.115 | 1.0692 | 1.0233 | 0.98467 | 0.946 | 0.90733 | 0.86867 | 0.83 | 0.8152 | 0.8004 | 0.7856 | 0.7708 | 0.756 | 0.73093 | 0.70587 | 0.6808 | 0.65573 | 0.63067 | 1.1682 | 46 | 1.1682 | 46
9.5 | 1.07 |  |  |  | 7.5 | 1.6805 | 1.5966 | 1.5126 | 1.4287 | 1.3448 | 1.2608 | 1.2429 | 1.225 | 1.2071 | 1.1892 | 1.1712 | 1.1533 | 1.1354 | 1.1175 | 1.0721 | 1.0267 | 0.98833 | 0.95 | 0.91167 | 0.87333 | 0.835 | 0.82 | 0.805 | 0.79 | 0.775 | 0.76 | 0.73467 | 0.70933 | 0.684 | 0.65867 | 0.63333 | 1.1712 | 47 | 1.1712 | 47
9.6 | 1.072 |  |  |  | 7.6 | 1.6878 | 1.6032 | 1.5186 | 1.434 | 1.3494 | 1.2647 | 1.2466 | 1.2286 | 1.2105 | 1.1924 | 1.1743 | 1.1562 | 1.1381 | 1.12 | 1.075 | 1.03 | 0.992 | 0.954 | 0.916 | 0.878 | 0.84 | 0.8248 | 0.8096 | 0.7944 | 0.7792 | 0.764 | 0.7384 | 0.7128 | 0.6872 | 0.6616 | 0.636 | 1.1743 | 48 | 1.1743 | 48
9.7 | 1.074 |  |  |  | 7.7 | 1.6951 | 1.6099 | 1.5246 | 1.4393 | 1.354 | 1.2687 | 1.2504 | 1.2321 | 1.2139 | 1.1956 | 1.1773 | 1.159 | 1.1408 | 1.1225 | 1.0779 | 1.0333 | 0.99567 | 0.958 | 0.92033 | 0.88267 | 0.845 | 0.8296 | 0.8142 | 0.7988 | 0.7834 | 0.768 | 0.74213 | 0.71627 | 0.6904 | 0.66453 | 0.63867 | 1.1773 | 49 | 1.1773 | 49
9.8 | 1.076 |  |  |  | 7.8 | 1.7025 | 1.6165 | 1.5305 | 1.4445 | 1.3586 | 1.2726 | 1.2541 | 1.2357 | 1.2172 | 1.1988 | 1.1803 | 1.1619 | 1.1434 | 1.125 | 1.0808 | 1.0367 | 0.99933 | 0.962 | 0.92467 | 0.88733 | 0.85 | 0.8344 | 0.8188 | 0.8032 | 0.7876 | 0.772 | 0.74587 | 0.71973 | 0.6936 | 0.66747 | 0.64133 | 1.1803 | 50 | 1.1803 | 50
9.9 | 1.078 |  |  |  | 7.9 | 1.7098 | 1.6231 | 1.5365 | 1.4498 | 1.3632 | 1.2765 | 1.2579 | 1.2393 | 1.2206 | 1.202 | 1.1834 | 1.1648 | 1.1461 | 1.1275 | 1.0837 | 1.04 | 1.003 | 0.966 | 0.929 | 0.892 | 0.855 | 0.8392 | 0.8234 | 0.8076 | 0.7918 | 0.776 | 0.7496 | 0.7232 | 0.6968 | 0.6704 | 0.644 | 1.1834 | 51 | 1.1834 | 51
10 | 1.08 |  |  |  | 8 | 1.7171 | 1.6297 | 1.5424 | 1.4551 | 1.3678 | 1.2804 | 1.2616 | 1.2428 | 1.224 | 1.2052 | 1.1864 | 1.1676 | 1.1488 | 1.13 | 1.0867 | 1.0433 | 1.0067 | 0.97 | 0.93333 | 0.89667 | 0.86 | 0.844 | 0.828 | 0.812 | 0.796 | 0.78 | 0.75333 | 0.72667 | 0.7 | 0.67333 | 0.64667 | 1.1864 | 52 | 1.1864 | 52
10.1 | 1.082 |  |  |  | 8.1 | 1.7244 | 1.6364 | 1.5484 | 1.4604 | 1.3724 | 1.2844 | 1.2654 | 1.2464 | 1.2274 | 1.2084 | 1.1894 | 1.1705 | 1.1515 | 1.1325 | 1.0896 | 1.0467 | 1.0103 | 0.974 | 0.93767 | 0.90133 | 0.865 | 0.8488 | 0.8326 | 0.8164 | 0.8002 | 0.784 | 0.75707 | 0.73013 | 0.7032 | 0.67627 | 0.64933 | 1.1894 | 53 | 1.1894 | 53
10.2 | 1.084 |  |  |  | 8.2 | 1.7317 | 1.643 | 1.5543 | 1.4656 | 1.377 | 1.2883 | 1.2691 | 1.25 | 1.2308 | 1.2116 | 1.1925 | 1.1733 | 1.1542 | 1.135 | 1.0925 | 1.05 | 1.014 | 0.978 | 0.942 | 0.906 | 0.87 | 0.8536 | 0.8372 | 0.8208 | 0.8044 | 0.788 | 0.7608 | 0.7336 | 0.7064 | 0.6792 | 0.652 | 1.1925 | 54 | 1.1925 | 54
10.3 | 1.086 |  |  |  | 8.3 | 1.739 | 1.6496 | 1.5603 | 1.4709 | 1.3816 | 1.2922 | 1.2729 | 1.2535 | 1.2342 | 1.2149 | 1.1955 | 1.1762 | 1.1568 | 1.1375 | 1.0954 | 1.0533 | 1.0177 | 0.982 | 0.94633 | 0.91067 | 0.875 | 0.8584 | 0.8418 | 0.8252 | 0.8086 | 0.792 | 0.76453 | 0.73707 | 0.7096 | 0.68213 | 0.65467 | 1.1955 | 55 | 1.1955 | 55
10.4 | 1.088 |  |  |  | 8.4 | 1.7463 | 1.6563 | 1.5662 | 1.4762 | 1.3862 | 1.2961 | 1.2766 | 1.2571 | 1.2376 | 1.2181 | 1.1985 | 1.179 | 1.1595 | 1.14 | 1.0983 | 1.0567 | 1.0213 | 0.986 | 0.95067 | 0.91533 | 0.88 | 0.8632 | 0.8464 | 0.8296 | 0.8128 | 0.796 | 0.76827 | 0.74053 | 0.7128 | 0.68507 | 0.65733 | 1.1985 | 56 | 1.1985 | 56
10.5 | 1.09 |  |  |  | 8.5 | 1.7536 | 1.6629 | 1.5722 | 1.4815 | 1.3908 | 1.3 | 1.2804 | 1.2607 | 1.241 | 1.2213 | 1.2016 | 1.1819 | 1.1622 | 1.1425 | 1.1013 | 1.06 | 1.025 | 0.99 | 0.955 | 0.92 | 0.885 | 0.868 | 0.851 | 0.834 | 0.817 | 0.8 | 0.772 | 0.744 | 0.716 | 0.688 | 0.66 | 1.2016 | 57 | 1.2016 | 57
10.6 | 1.092 |  |  |  | 8.6 | 1.7609 | 1.6695 | 1.5781 | 1.4867 | 1.3954 | 1.304 | 1.2841 | 1.2642 | 1.2444 | 1.2245 | 1.2046 | 1.1847 | 1.1649 | 1.145 | 1.1042 | 1.0633 | 1.0287 | 0.994 | 0.95933 | 0.92467 | 0.89 | 0.8728 | 0.8556 | 0.8384 | 0.8212 | 0.804 | 0.77573 | 0.74747 | 0.7192 | 0.69093 | 0.66267 | 1.2046 | 58 | 1.2046 | 58
10.7 | 1.094 |  |  |  | 8.7 | 1.7682 | 1.6762 | 1.5841 | 1.492 | 1.4 | 1.3079 | 1.2878 | 1.2678 | 1.2477 | 1.2277 | 1.2076 | 1.1876 | 1.1675 | 1.1475 | 1.1071 | 1.0667 | 1.0323 | 0.998 | 0.96367 | 0.92933 | 0.895 | 0.8776 | 0.8602 | 0.8428 | 0.8254 | 0.808 | 0.77947 | 0.75093 | 0.7224 | 0.69387 | 0.66533 | 1.2076 | 59 | 1.2076 | 59
10.8 | 1.096 |  |  |  | 8.8 | 1.7755 | 1.6828 | 1.59 | 1.4973 | 1.4046 | 1.3118 | 1.2916 | 1.2714 | 1.2511 | 1.2309 | 1.2107 | 1.1905 | 1.1702 | 1.15 | 1.11 | 1.07 | 1.036 | 1.002 | 0.968 | 0.934 | 0.9 | 0.8824 | 0.8648 | 0.8472 | 0.8296 | 0.812 | 0.7832 | 0.7544 | 0.7256 | 0.6968 | 0.668 | 1.2107 | 60 | 1.2107 | 60
10.9 | 1.098 |  |  |  | 8.9 | 1.7828 | 1.6894 | 1.596 | 1.5026 | 1.4092 | 1.3157 | 1.2953 | 1.2749 | 1.2545 | 1.2341 | 1.2137 | 1.1933 | 1.1729 | 1.1525 | 1.1129 | 1.0733 | 1.0397 | 1.006 | 0.97233 | 0.93867 | 0.905 | 0.8872 | 0.8694 | 0.8516 | 0.8338 | 0.816 | 0.78693 | 0.75787 | 0.7288 | 0.69973 | 0.67067 | 1.2137 | 61 | 1.2137 | 61
11 | 1.1 |  |  |  | 9 | 1.7901 | 1.696 | 1.6019 | 1.5079 | 1.4138 | 1.3197 | 1.2991 | 1.2785 | 1.2579 | 1.2373 | 1.2167 | 1.1962 | 1.1756 | 1.155 | 1.1158 | 1.0767 | 1.0433 | 1.01 | 0.97667 | 0.94333 | 0.91 | 0.892 | 0.874 | 0.856 | 0.838 | 0.82 | 0.79067 | 0.76133 | 0.732 | 0.70267 | 0.67333 | 1.2167 | 62 | 1.2167 | 62
11.1 | 1.102 |  |  |  | 9.1 | 1.7974 | 1.7027 | 1.6079 | 1.5131 | 1.4184 | 1.3236 | 1.3028 | 1.2821 | 1.2613 | 1.2405 | 1.2198 | 1.199 | 1.1783 | 1.1575 | 1.1187 | 1.08 | 1.047 | 1.014 | 0.981 | 0.948 | 0.915 | 0.8968 | 0.8786 | 0.8604 | 0.8422 | 0.824 | 0.7944 | 0.7648 | 0.7352 | 0.7056 | 0.676 | 1.2198 | 63 | 1.2198 | 63
11.2 | 1.104 |  |  |  | 9.2 | 1.8047 | 1.7093 | 1.6139 | 1.5184 | 1.423 | 1.3275 | 1.3066 | 1.2856 | 1.2647 | 1.2438 | 1.2228 | 1.2019 | 1.1809 | 1.16 | 1.1217 | 1.0833 | 1.0507 | 1.018 | 0.98533 | 0.95267 | 0.92 | 0.9016 | 0.8832 | 0.8648 | 0.8464 | 0.828 | 0.79813 | 0.76827 | 0.7384 | 0.70853 | 0.67867 | 1.2228 | 64 | 1.2228 | 64
11.3 | 1.106 |  |  |  | 9.3 | 1.8121 | 1.7159 | 1.6198 | 1.5237 | 1.4276 | 1.3314 | 1.3103 | 1.2892 | 1.2681 | 1.247 | 1.2259 | 1.2047 | 1.1836 | 1.1625 | 1.1246 | 1.0867 | 1.0543 | 1.022 | 0.98967 | 0.95733 | 0.925 | 0.9064 | 0.8878 | 0.8692 | 0.8506 | 0.832 | 0.80187 | 0.77173 | 0.7416 | 0.71147 | 0.68133 | 1.2259 | 65 | 1.2259 | 65
11.4 | 1.108 |  |  |  | 9.4 | 1.8194 | 1.7226 | 1.6258 | 1.529 | 1.4322 | 1.3354 | 1.3141 | 1.2928 | 1.2715 | 1.2502 | 1.2289 | 1.2076 | 1.1863 | 1.165 | 1.1275 | 1.09 | 1.058 | 1.026 | 0.994 | 0.962 | 0.93 | 0.9112 | 0.8924 | 0.8736 | 0.8548 | 0.836 | 0.8056 | 0.7752 | 0.7448 | 0.7144 | 0.684 | 1.2289 | 66 | 1.2289 | 66
11.5 | 1.11 |  |  |  | 9.5 | 1.8267 | 1.7292 | 1.6317 | 1.5342 | 1.4368 | 1.3393 | 1.3178 | 1.2963 | 1.2749 | 1.2534 | 1.2319 | 1.2104 | 1.189 | 1.1675 | 1.1304 | 1.0933 | 1.0617 | 1.03 | 0.99833 | 0.96667 | 0.935 | 0.916 | 0.897 | 0.878 | 0.859 | 0.84 | 0.80933 | 0.77867 | 0.748 | 0.71733 | 0.68667 | 1.2319 | 67 | 1.2319 | 67
11.6 | 1.112 |  |  |  | 9.6 | 1.834 | 1.7358 | 1.6377 | 1.5395 | 1.4414 | 1.3432 | 1.3216 | 1.2999 | 1.2783 | 1.2566 | 1.235 | 1.2133 | 1.1917 | 1.17 | 1.1333 | 1.0967 | 1.0653 | 1.034 | 1.0027 | 0.97133 | 0.94 | 0.9208 | 0.9016 | 0.8824 | 0.8632 | 0.844 | 0.81307 | 0.78213 | 0.7512 | 0.72027 | 0.68933 | 1.235 | 68 | 1.235 | 68
11.7 | 1.114 |  |  |  | 9.7 | 1.8413 | 1.7425 | 1.6436 | 1.5448 | 1.446 | 1.3471 | 1.3253 | 1.3035 | 1.2816 | 1.2598 | 1.238 | 1.2162 | 1.1943 | 1.1725 | 1.1362 | 1.1 | 1.069 | 1.038 | 1.007 | 0.976 | 0.945 | 0.9256 | 0.9062 | 0.8868 | 0.8674 | 0.848 | 0.8168 | 0.7856 | 0.7544 | 0.7232 | 0.692 | 1.238 | 69 | 1.238 | 69
11.8 | 1.116 |  |  |  | 9.8 | 1.8486 | 1.7491 | 1.6496 | 1.5501 | 1.4506 | 1.3511 | 1.329 | 1.307 | 1.285 | 1.263 | 1.241 | 1.219 | 1.197 | 1.175 | 1.1392 | 1.1033 | 1.0727 | 1.042 | 1.0113 | 0.98067 | 0.95 | 0.9304 | 0.9108 | 0.8912 | 0.8716 | 0.852 | 0.82053 | 0.78907 | 0.7576 | 0.72613 | 0.69467 | 1.241 | 70 | 1.241 | 70
11.9 | 1.118 |  |  |  | 9.9 | 1.8559 | 1.7557 | 1.6555 | 1.5553 | 1.4552 | 1.355 | 1.3328 | 1.3106 | 1.2884 | 1.2662 | 1.2441 | 1.2219 | 1.1997 | 1.1775 | 1.1421 | 1.1067 | 1.0763 | 1.046 | 1.0157 | 0.98533 | 0.955 | 0.9352 | 0.9154 | 0.8956 | 0.8758 | 0.856 | 0.82427 | 0.79253 | 0.7608 | 0.72907 | 0.69733 | 1.2441 | 71 | 1.2441 | 71
12 | 1.12 |  |  |  | 10 | 1.8632 | 1.7623 | 1.6615 | 1.5606 | 1.4598 | 1.3589 | 1.3365 | 1.3142 | 1.2918 | 1.2694 | 1.2471 | 1.2247 | 1.2024 | 1.18 | 1.145 | 1.11 | 1.08 | 1.05 | 1.02 | 0.99 | 0.96 | 0.94 | 0.92 | 0.9 | 0.88 | 0.86 | 0.828 | 0.796 | 0.764 | 0.732 | 0.7 | 1.2471 | 72 | 1.2471 | 72
12.1 | 1.121
12.2 | 1.122
12.3 | 1.123 | [35 empty] | Max | 1.2471 | Max | 1.2471
12.4 | 1.124 | [35 empty] | Min | 0.93875 | Min | 0.93875
12.5 | 1.125
12.6 | 1.126
12.7 | 1.127
12.8 | 1.128
12.9 | 1.129
13 | 1.13
13.1 | 1.132
13.2 | 1.134
13.3 | 1.136
13.4 | 1.138
13.5 | 1.14
13.6 | 1.142
13.7 | 1.144
13.8 | 1.146
13.9 | 1.148
14 | 1.15
14.1 | 1.151
14.2 | 1.152
14.3 | 1.153
14.4 | 1.154
14.5 | 1.155
14.6 | 1.156
14.7 | 1.157
14.8 | 1.158
14.9 | 1.159
15 | 1.16
15.1 | 1.161
15.2 | 1.162
15.3 | 1.163
15.4 | 1.164
15.5 | 1.165
15.6 | 1.166
15.7 | 1.167
15.8 | 1.168
15.9 | 1.169
16 | 1.17
Ambient Vs PDP
Ambient Temp (°C) | RH = 26% | Row number for water content
10 | -8 | 65
12 | -6 | 67
14 | -5 | 68
16 | -3 | 70
18 | -2 | 71
20 | 0 | 73
22 | 1 | 74
24 | 3 | 76
26 | 4 | 77
28 | 6 | 79
30 | 8 | 81
32 | 9 | 82
34 | 11 | 84
36 | 13 | 86
38 | 14 | 87
40 | 16 | 89
42 | 18 | 91
44 | 19 | 92
46 | 21 | 94
48 | 23 | 96
50 | 24 | 97
52 | 26 | 99
54 | 28 | 101
56 | 29 | 102

## Correction Factors50HZ (hidden)
Pressure Correction |  |  | Ambient Correction |  | PDP Inlet Correction
Inlet pressure | Correction factor |  | Ambient temperature | Correction factor |  | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | Relevant Column |  | Relevant Column
5 | 0.9 |  | 25 | 1 | 3 | 1.57 | 1.504 | 1.438 | 1.372 | 1.306 | 1.24 | 1.192 | 1.144 | 1.096 | 1.048 | 1 | 0.964 | 0.928 | 0.892 | 0.856 | 0.82 | 0.794 | 0.768 | 0.742 | 0.716 | 0.69 | 0.672 | 0.654 | 0.636 | 0.618 | 0.6 | 0.578 | 0.556 | 0.534 | 0.512 | 0.49 | 1 | 2 | 1 | 2
5.1 | 0.906 |  | 26 | 0.984 | 3.1 | 1.5778 | 1.5114 | 1.4449 | 1.3785 | 1.312 | 1.2456 | 1.198 | 1.1503 | 1.1027 | 1.0551 | 1.0075 | 0.971 | 0.9345 | 0.898 | 0.8615 | 0.825 | 0.7987 | 0.7724 | 0.7461 | 0.7198 | 0.6935 | 0.6755 | 0.6575 | 0.6395 | 0.6215 | 0.6035 | 0.5815 | 0.5595 | 0.5375 | 0.5155 | 0.4935 | 1.0075 | 3 | 1.0075 | 3
5.2 | 0.912 |  | 27 | 0.968 | 3.2 | 1.5857 | 1.5188 | 1.4519 | 1.385 | 1.3181 | 1.2512 | 1.2039 | 1.1567 | 1.1095 | 1.0622 | 1.015 | 0.978 | 0.941 | 0.904 | 0.867 | 0.83 | 0.8034 | 0.7768 | 0.7502 | 0.7236 | 0.697 | 0.679 | 0.661 | 0.643 | 0.625 | 0.607 | 0.585 | 0.563 | 0.541 | 0.519 | 0.497 | 1.015 | 4 | 1.015 | 4
5.3 | 0.918 |  | 28 | 0.952 | 3.3 | 1.5936 | 1.5262 | 1.4588 | 1.3915 | 1.3241 | 1.2567 | 1.2099 | 1.163 | 1.1162 | 1.0693 | 1.0225 | 0.985 | 0.9475 | 0.91 | 0.8725 | 0.835 | 0.8081 | 0.7812 | 0.7543 | 0.7274 | 0.7005 | 0.6825 | 0.6645 | 0.6465 | 0.6285 | 0.6105 | 0.5885 | 0.5665 | 0.5445 | 0.5225 | 0.5005 | 1.0225 | 5 | 1.0225 | 5
5.4 | 0.924 |  | 29 | 0.936 | 3.4 | 1.6014 | 1.5336 | 1.4658 | 1.398 | 1.3301 | 1.2623 | 1.2159 | 1.1694 | 1.1229 | 1.0765 | 1.03 | 0.992 | 0.954 | 0.916 | 0.878 | 0.84 | 0.8128 | 0.7856 | 0.7584 | 0.7312 | 0.704 | 0.686 | 0.668 | 0.65 | 0.632 | 0.614 | 0.592 | 0.57 | 0.548 | 0.526 | 0.504 | 1.03 | 6 | 1.03 | 6
5.5 | 0.93 |  | 30 | 0.92 | 3.5 | 1.6093 | 1.541 | 1.4727 | 1.4044 | 1.3362 | 1.2679 | 1.2218 | 1.1757 | 1.1297 | 1.0836 | 1.0375 | 0.999 | 0.9605 | 0.922 | 0.8835 | 0.845 | 0.8175 | 0.79 | 0.7625 | 0.735 | 0.7075 | 0.6895 | 0.6715 | 0.6535 | 0.6355 | 0.6175 | 0.5955 | 0.5735 | 0.5515 | 0.5295 | 0.5075 | 1.0375 | 7 | 1.0375 | 7
5.6 | 0.936 |  | 31 | 0.904 | 3.6 | 1.6171 | 1.5484 | 1.4797 | 1.4109 | 1.3422 | 1.2735 | 1.2278 | 1.1821 | 1.1364 | 1.0907 | 1.045 | 1.006 | 0.967 | 0.928 | 0.889 | 0.85 | 0.8222 | 0.7944 | 0.7666 | 0.7388 | 0.711 | 0.693 | 0.675 | 0.657 | 0.639 | 0.621 | 0.599 | 0.577 | 0.555 | 0.533 | 0.511 | 1.045 | 8 | 1.045 | 8
5.7 | 0.942 |  | 32 | 0.888 | 3.7 | 1.6249 | 1.5558 | 1.4866 | 1.4174 | 1.3482 | 1.2791 | 1.2337 | 1.1884 | 1.1431 | 1.0978 | 1.0525 | 1.013 | 0.9735 | 0.934 | 0.8945 | 0.855 | 0.8269 | 0.7988 | 0.7707 | 0.7426 | 0.7145 | 0.6965 | 0.6785 | 0.6605 | 0.6425 | 0.6245 | 0.6025 | 0.5805 | 0.5585 | 0.5365 | 0.5145 | 1.0525 | 9 | 1.0525 | 9
5.8 | 0.948 |  | 33 | 0.872 | 3.8 | 1.6328 | 1.5632 | 1.4935 | 1.4239 | 1.3543 | 1.2846 | 1.2397 | 1.1948 | 1.1499 | 1.1049 | 1.06 | 1.02 | 0.98 | 0.94 | 0.9 | 0.86 | 0.8316 | 0.8032 | 0.7748 | 0.7464 | 0.718 | 0.7 | 0.682 | 0.664 | 0.646 | 0.628 | 0.606 | 0.584 | 0.562 | 0.54 | 0.518 | 1.06 | 10 | 1.06 | 10
5.9 | 0.954 |  | 34 | 0.856 | 3.9 | 1.6406 | 1.5706 | 1.5005 | 1.4304 | 1.3603 | 1.2902 | 1.2457 | 1.2011 | 1.1566 | 1.112 | 1.0675 | 1.027 | 0.9865 | 0.946 | 0.9055 | 0.865 | 0.8363 | 0.8076 | 0.7789 | 0.7502 | 0.7215 | 0.7035 | 0.6855 | 0.6675 | 0.6495 | 0.6315 | 0.6095 | 0.5875 | 0.5655 | 0.5435 | 0.5215 | 1.0675 | 11 | 1.0675 | 11
6 | 0.96 |  | 35 | 0.84 | 4 | 1.6485 | 1.578 | 1.5074 | 1.4369 | 1.3663 | 1.2958 | 1.2516 | 1.2075 | 1.1633 | 1.1192 | 1.075 | 1.034 | 0.993 | 0.952 | 0.911 | 0.87 | 0.841 | 0.812 | 0.783 | 0.754 | 0.725 | 0.707 | 0.689 | 0.671 | 0.653 | 0.635 | 0.613 | 0.591 | 0.569 | 0.547 | 0.525 | 1.075 | 12 | 1.075 | 12
6.1 | 0.964 |  | 36 | 0.832 | 4.1 | 1.6563 | 1.5854 | 1.5144 | 1.4434 | 1.3724 | 1.3014 | 1.2576 | 1.2138 | 1.1701 | 1.1263 | 1.0825 | 1.041 | 0.9995 | 0.958 | 0.9165 | 0.875 | 0.8457 | 0.8164 | 0.7871 | 0.7578 | 0.7285 | 0.7105 | 0.6925 | 0.6745 | 0.6565 | 0.6385 | 0.6165 | 0.5945 | 0.5725 | 0.5505 | 0.5285 | 1.0825 | 13 | 1.0825 | 13
6.2 | 0.968 |  | 37 | 0.824 | 4.2 | 1.6642 | 1.5928 | 1.5213 | 1.4499 | 1.3784 | 1.307 | 1.2636 | 1.2202 | 1.1768 | 1.1334 | 1.09 | 1.048 | 1.006 | 0.964 | 0.922 | 0.88 | 0.8504 | 0.8208 | 0.7912 | 0.7616 | 0.732 | 0.714 | 0.696 | 0.678 | 0.66 | 0.642 | 0.62 | 0.598 | 0.576 | 0.554 | 0.532 | 1.09 | 14 | 1.09 | 14
6.3 | 0.972 |  | 38 | 0.816 | 4.3 | 1.6721 | 1.6001 | 1.5282 | 1.4563 | 1.3844 | 1.3125 | 1.2695 | 1.2265 | 1.1835 | 1.1405 | 1.0975 | 1.055 | 1.0125 | 0.97 | 0.9275 | 0.885 | 0.8551 | 0.8252 | 0.7953 | 0.7654 | 0.7355 | 0.7175 | 0.6995 | 0.6815 | 0.6635 | 0.6455 | 0.6235 | 0.6015 | 0.5795 | 0.5575 | 0.5355 | 1.0975 | 15 | 1.0975 | 15
6.4 | 0.976 |  | 39 | 0.808 | 4.4 | 1.6799 | 1.6075 | 1.5352 | 1.4628 | 1.3905 | 1.3181 | 1.2755 | 1.2329 | 1.1902 | 1.1476 | 1.105 | 1.062 | 1.019 | 0.976 | 0.933 | 0.89 | 0.8598 | 0.8296 | 0.7994 | 0.7692 | 0.739 | 0.721 | 0.703 | 0.685 | 0.667 | 0.649 | 0.627 | 0.605 | 0.583 | 0.561 | 0.539 | 1.105 | 16 | 1.105 | 16
6.5 | 0.98 |  | 40 | 0.8 | 4.5 | 1.6878 | 1.6149 | 1.5421 | 1.4693 | 1.3965 | 1.3237 | 1.2815 | 1.2392 | 1.197 | 1.1547 | 1.1125 | 1.069 | 1.0255 | 0.982 | 0.9385 | 0.895 | 0.8645 | 0.834 | 0.8035 | 0.773 | 0.7425 | 0.7245 | 0.7065 | 0.6885 | 0.6705 | 0.6525 | 0.6305 | 0.6085 | 0.5865 | 0.5645 | 0.5425 | 1.1125 | 17 | 1.1125 | 17
6.6 | 0.984 |  | 41 | 0.788 | 4.6 | 1.6956 | 1.6223 | 1.5491 | 1.4758 | 1.4025 | 1.3293 | 1.2874 | 1.2456 | 1.2037 | 1.1619 | 1.12 | 1.076 | 1.032 | 0.988 | 0.944 | 0.9 | 0.8692 | 0.8384 | 0.8076 | 0.7768 | 0.746 | 0.728 | 0.71 | 0.692 | 0.674 | 0.656 | 0.634 | 0.612 | 0.59 | 0.568 | 0.546 | 1.12 | 18 | 1.12 | 18
6.7 | 0.988 |  | 42 | 0.776 | 4.7 | 1.7034 | 1.6297 | 1.556 | 1.4823 | 1.4086 | 1.3349 | 1.2934 | 1.2519 | 1.2104 | 1.169 | 1.1275 | 1.083 | 1.0385 | 0.994 | 0.9495 | 0.905 | 0.8739 | 0.8428 | 0.8117 | 0.7806 | 0.7495 | 0.7315 | 0.7135 | 0.6955 | 0.6775 | 0.6595 | 0.6375 | 0.6155 | 0.5935 | 0.5715 | 0.5495 | 1.1275 | 19 | 1.1275 | 19
6.8 | 0.992 |  | 43 | 0.764 | 4.8 | 1.7113 | 1.6371 | 1.563 | 1.4888 | 1.4146 | 1.3404 | 1.2994 | 1.2583 | 1.2172 | 1.1761 | 1.135 | 1.09 | 1.045 | 1 | 0.955 | 0.91 | 0.8786 | 0.8472 | 0.8158 | 0.7844 | 0.753 | 0.735 | 0.717 | 0.699 | 0.681 | 0.663 | 0.641 | 0.619 | 0.597 | 0.575 | 0.553 | 1.135 | 20 | 1.135 | 20
6.9 | 0.996 |  | 44 | 0.752 | 4.9 | 1.7191 | 1.6445 | 1.5699 | 1.4953 | 1.4206 | 1.346 | 1.3053 | 1.2646 | 1.2239 | 1.1832 | 1.1425 | 1.097 | 1.0515 | 1.006 | 0.9605 | 0.915 | 0.8833 | 0.8516 | 0.8199 | 0.7882 | 0.7565 | 0.7385 | 0.7205 | 0.7025 | 0.6845 | 0.6665 | 0.6445 | 0.6225 | 0.6005 | 0.5785 | 0.5565 | 1.1425 | 21 | 1.1425 | 21
7 | 1 |  | 45 | 0.74 | 5 | 1.727 | 1.6519 | 1.5768 | 1.5018 | 1.4267 | 1.3516 | 1.3113 | 1.271 | 1.2306 | 1.1903 | 1.15 | 1.104 | 1.058 | 1.012 | 0.966 | 0.92 | 0.888 | 0.856 | 0.824 | 0.792 | 0.76 | 0.742 | 0.724 | 0.706 | 0.688 | 0.67 | 0.648 | 0.626 | 0.604 | 0.582 | 0.56 | 1.15 | 22 | 1.15 | 22
7.1 | 1.003 |  |  |  | 5.1 | 1.7349 | 1.6591 | 1.5833 | 1.5075 | 1.4317 | 1.3559 | 1.3158 | 1.2756 | 1.2354 | 1.1952 | 1.155 | 1.1089 | 1.0628 | 1.0167 | 0.9706 | 0.9245 | 0.8921 | 0.8597 | 0.8273 | 0.7949 | 0.7625 | 0.7447 | 0.7269 | 0.7091 | 0.6913 | 0.6735 | 0.6514 | 0.6293 | 0.6072 | 0.5851 | 0.563 | 1.155 | 23 | 1.155 | 23
7.2 | 1.006 |  |  |  | 5.2 | 1.7427 | 1.6662 | 1.5897 | 1.5132 | 1.4368 | 1.3603 | 1.3202 | 1.2802 | 1.2401 | 1.2001 | 1.16 | 1.1138 | 1.0676 | 1.0214 | 0.9752 | 0.929 | 0.8962 | 0.8634 | 0.8306 | 0.7978 | 0.765 | 0.7474 | 0.7298 | 0.7122 | 0.6946 | 0.677 | 0.6548 | 0.6326 | 0.6104 | 0.5882 | 0.566 | 1.16 | 24 | 1.16 | 24
7.3 | 1.009 |  |  |  | 5.3 | 1.7506 | 1.6734 | 1.5962 | 1.519 | 1.4418 | 1.3646 | 1.3247 | 1.2848 | 1.2448 | 1.2049 | 1.165 | 1.1187 | 1.0724 | 1.0261 | 0.9798 | 0.9335 | 0.9003 | 0.8671 | 0.8339 | 0.8007 | 0.7675 | 0.7501 | 0.7327 | 0.7153 | 0.6979 | 0.6805 | 0.6582 | 0.6359 | 0.6136 | 0.5913 | 0.569 | 1.165 | 25 | 1.165 | 25
7.4 | 1.012 |  |  |  | 5.4 | 1.7584 | 1.6805 | 1.6026 | 1.5247 | 1.4468 | 1.369 | 1.3292 | 1.2894 | 1.2496 | 1.2098 | 1.17 | 1.1236 | 1.0772 | 1.0308 | 0.9844 | 0.938 | 0.9044 | 0.8708 | 0.8372 | 0.8036 | 0.77 | 0.7528 | 0.7356 | 0.7184 | 0.7012 | 0.684 | 0.6616 | 0.6392 | 0.6168 | 0.5944 | 0.572 | 1.17 | 26 | 1.17 | 26
7.5 | 1.015 |  |  |  | 5.5 | 1.7663 | 1.6877 | 1.6091 | 1.5305 | 1.4519 | 1.3733 | 1.3336 | 1.294 | 1.2543 | 1.2147 | 1.175 | 1.1285 | 1.082 | 1.0355 | 0.989 | 0.9425 | 0.9085 | 0.8745 | 0.8405 | 0.8065 | 0.7725 | 0.7555 | 0.7385 | 0.7215 | 0.7045 | 0.6875 | 0.665 | 0.6425 | 0.62 | 0.5975 | 0.575 | 1.175 | 27 | 1.175 | 27
7.6 | 1.018 |  |  |  | 5.6 | 1.7741 | 1.6948 | 1.6155 | 1.5362 | 1.4569 | 1.3776 | 1.3381 | 1.2986 | 1.2591 | 1.2195 | 1.18 | 1.1334 | 1.0868 | 1.0402 | 0.9936 | 0.947 | 0.9126 | 0.8782 | 0.8438 | 0.8094 | 0.775 | 0.7582 | 0.7414 | 0.7246 | 0.7078 | 0.691 | 0.6684 | 0.6458 | 0.6232 | 0.6006 | 0.578 | 1.18 | 28 | 1.18 | 28
7.7 | 1.021 |  |  |  | 5.7 | 1.7819 | 1.702 | 1.622 | 1.542 | 1.462 | 1.382 | 1.3426 | 1.3032 | 1.2638 | 1.2244 | 1.185 | 1.1383 | 1.0916 | 1.0449 | 0.9982 | 0.9515 | 0.9167 | 0.8819 | 0.8471 | 0.8123 | 0.7775 | 0.7609 | 0.7443 | 0.7277 | 0.7111 | 0.6945 | 0.6718 | 0.6491 | 0.6264 | 0.6037 | 0.581 | 1.185 | 29 | 1.185 | 29
7.8 | 1.024 |  |  |  | 5.8 | 1.7898 | 1.7091 | 1.6284 | 1.5477 | 1.467 | 1.3863 | 1.3471 | 1.3078 | 1.2685 | 1.2293 | 1.19 | 1.1432 | 1.0964 | 1.0496 | 1.0028 | 0.956 | 0.9208 | 0.8856 | 0.8504 | 0.8152 | 0.78 | 0.7636 | 0.7472 | 0.7308 | 0.7144 | 0.698 | 0.6752 | 0.6524 | 0.6296 | 0.6068 | 0.584 | 1.19 | 30 | 1.19 | 30
7.9 | 1.027 |  |  |  | 5.9 | 1.7976 | 1.7163 | 1.6349 | 1.5535 | 1.4721 | 1.3907 | 1.3515 | 1.3124 | 1.2733 | 1.2341 | 1.195 | 1.1481 | 1.1012 | 1.0543 | 1.0074 | 0.9605 | 0.9249 | 0.8893 | 0.8537 | 0.8181 | 0.7825 | 0.7663 | 0.7501 | 0.7339 | 0.7177 | 0.7015 | 0.6786 | 0.6557 | 0.6328 | 0.6099 | 0.587 | 1.195 | 31 | 1.195 | 31
8 | 1.03 |  |  |  | 6 | 1.8055 | 1.7234 | 1.6413 | 1.5592 | 1.4771 | 1.395 | 1.356 | 1.317 | 1.278 | 1.239 | 1.2 | 1.153 | 1.106 | 1.059 | 1.012 | 0.965 | 0.929 | 0.893 | 0.857 | 0.821 | 0.785 | 0.769 | 0.753 | 0.737 | 0.721 | 0.705 | 0.682 | 0.659 | 0.636 | 0.613 | 0.59 | 1.2 | 32 | 1.2 | 32
8.1 | 1.033 |  |  |  | 6.1 | 1.8134 | 1.7305 | 1.6477 | 1.5649 | 1.4821 | 1.3993 | 1.3605 | 1.3216 | 1.2827 | 1.2439 | 1.205 | 1.1579 | 1.1108 | 1.0637 | 1.0166 | 0.9695 | 0.9331 | 0.8967 | 0.8603 | 0.8239 | 0.7875 | 0.7717 | 0.7559 | 0.7401 | 0.7243 | 0.7085 | 0.6854 | 0.6623 | 0.6392 | 0.6161 | 0.593 | 1.205 | 33 | 1.205 | 33
8.2 | 1.036 |  |  |  | 6.2 | 1.8212 | 1.7377 | 1.6542 | 1.5707 | 1.4872 | 1.4037 | 1.3649 | 1.3262 | 1.2875 | 1.2487 | 1.21 | 1.1628 | 1.1156 | 1.0684 | 1.0212 | 0.974 | 0.9372 | 0.9004 | 0.8636 | 0.8268 | 0.79 | 0.7744 | 0.7588 | 0.7432 | 0.7276 | 0.712 | 0.6888 | 0.6656 | 0.6424 | 0.6192 | 0.596 | 1.21 | 34 | 1.21 | 34
8.3 | 1.039 |  |  |  | 6.3 | 1.8291 | 1.7448 | 1.6606 | 1.5764 | 1.4922 | 1.408 | 1.3694 | 1.3308 | 1.2922 | 1.2536 | 1.215 | 1.1677 | 1.1204 | 1.0731 | 1.0258 | 0.9785 | 0.9413 | 0.9041 | 0.8669 | 0.8297 | 0.7925 | 0.7771 | 0.7617 | 0.7463 | 0.7309 | 0.7155 | 0.6922 | 0.6689 | 0.6456 | 0.6223 | 0.599 | 1.215 | 35 | 1.215 | 35
8.4 | 1.042 |  |  |  | 6.4 | 1.8369 | 1.752 | 1.6671 | 1.5822 | 1.4973 | 1.4124 | 1.3739 | 1.3354 | 1.2969 | 1.2585 | 1.22 | 1.1726 | 1.1252 | 1.0778 | 1.0304 | 0.983 | 0.9454 | 0.9078 | 0.8702 | 0.8326 | 0.795 | 0.7798 | 0.7646 | 0.7494 | 0.7342 | 0.719 | 0.6956 | 0.6722 | 0.6488 | 0.6254 | 0.602 | 1.22 | 36 | 1.22 | 36
8.5 | 1.045 |  |  |  | 6.5 | 1.8447 | 1.7591 | 1.6735 | 1.5879 | 1.5023 | 1.4167 | 1.3784 | 1.34 | 1.3017 | 1.2633 | 1.225 | 1.1775 | 1.13 | 1.0825 | 1.035 | 0.9875 | 0.9495 | 0.9115 | 0.8735 | 0.8355 | 0.7975 | 0.7825 | 0.7675 | 0.7525 | 0.7375 | 0.7225 | 0.699 | 0.6755 | 0.652 | 0.6285 | 0.605 | 1.225 | 37 | 1.225 | 37
8.6 | 1.048 |  |  |  | 6.6 | 1.8526 | 1.7663 | 1.68 | 1.5937 | 1.5074 | 1.421 | 1.3828 | 1.3446 | 1.3064 | 1.2682 | 1.23 | 1.1824 | 1.1348 | 1.0872 | 1.0396 | 0.992 | 0.9536 | 0.9152 | 0.8768 | 0.8384 | 0.8 | 0.7852 | 0.7704 | 0.7556 | 0.7408 | 0.726 | 0.7024 | 0.6788 | 0.6552 | 0.6316 | 0.608 | 1.23 | 38 | 1.23 | 38
8.7 | 1.051 |  |  |  | 6.7 | 1.8604 | 1.7734 | 1.6864 | 1.5994 | 1.5124 | 1.4254 | 1.3873 | 1.3492 | 1.3112 | 1.2731 | 1.235 | 1.1873 | 1.1396 | 1.0919 | 1.0442 | 0.9965 | 0.9577 | 0.9189 | 0.8801 | 0.8413 | 0.8025 | 0.7879 | 0.7733 | 0.7587 | 0.7441 | 0.7295 | 0.7058 | 0.6821 | 0.6584 | 0.6347 | 0.611 | 1.235 | 39 | 1.235 | 39
8.8 | 1.054 |  |  |  | 6.8 | 1.8683 | 1.7806 | 1.6929 | 1.6052 | 1.5174 | 1.4297 | 1.3918 | 1.3538 | 1.3159 | 1.2779 | 1.24 | 1.1922 | 1.1444 | 1.0966 | 1.0488 | 1.001 | 0.9618 | 0.9226 | 0.8834 | 0.8442 | 0.805 | 0.7906 | 0.7762 | 0.7618 | 0.7474 | 0.733 | 0.7092 | 0.6854 | 0.6616 | 0.6378 | 0.614 | 1.24 | 40 | 1.24 | 40
8.9 | 1.057 |  |  |  | 6.9 | 1.8761 | 1.7877 | 1.6993 | 1.6109 | 1.5225 | 1.4341 | 1.3962 | 1.3584 | 1.3206 | 1.2828 | 1.245 | 1.1971 | 1.1492 | 1.1013 | 1.0534 | 1.0055 | 0.9659 | 0.9263 | 0.8867 | 0.8471 | 0.8075 | 0.7933 | 0.7791 | 0.7649 | 0.7507 | 0.7365 | 0.7126 | 0.6887 | 0.6648 | 0.6409 | 0.617 | 1.245 | 41 | 1.245 | 41
9 | 1.06 |  |  |  | 7 | 1.884 | 1.7949 | 1.7058 | 1.6166 | 1.5275 | 1.4384 | 1.4007 | 1.363 | 1.3254 | 1.2877 | 1.25 | 1.202 | 1.154 | 1.106 | 1.058 | 1.01 | 0.97 | 0.93 | 0.89 | 0.85 | 0.81 | 0.796 | 0.782 | 0.768 | 0.754 | 0.74 | 0.716 | 0.692 | 0.668 | 0.644 | 0.62 | 1.25 | 42 | 1.25 | 42
9.1 | 1.062 |  |  |  | 7.1 | 1.8924 | 1.8025 | 1.7126 | 1.6227 | 1.5328 | 1.4429 | 1.4052 | 1.3675 | 1.3298 | 1.2921 | 1.2543 | 1.2061 | 1.1579 | 1.1097 | 1.0615 | 1.0133 | 0.97367 | 0.934 | 0.89433 | 0.85467 | 0.815 | 0.8008 | 0.7866 | 0.7724 | 0.7582 | 0.744 | 0.71973 | 0.69547 | 0.6712 | 0.64693 | 0.62267 | 1.2543 | 43 | 1.2543 | 43
9.2 | 1.064 |  |  |  | 7.2 | 1.9007 | 1.8101 | 1.7194 | 1.6288 | 1.5381 | 1.4475 | 1.4097 | 1.372 | 1.3342 | 1.2964 | 1.2587 | 1.2103 | 1.1619 | 1.1135 | 1.0651 | 1.0167 | 0.97733 | 0.938 | 0.89867 | 0.85933 | 0.82 | 0.8056 | 0.7912 | 0.7768 | 0.7624 | 0.748 | 0.72347 | 0.69893 | 0.6744 | 0.64987 | 0.62533 | 1.2587 | 44 | 1.2587 | 44
9.3 | 1.066 |  |  |  | 7.3 | 1.9091 | 1.8177 | 1.7263 | 1.6349 | 1.5435 | 1.452 | 1.4142 | 1.3764 | 1.3386 | 1.3008 | 1.263 | 1.2144 | 1.1658 | 1.1172 | 1.0686 | 1.02 | 0.981 | 0.942 | 0.903 | 0.864 | 0.825 | 0.8104 | 0.7958 | 0.7812 | 0.7666 | 0.752 | 0.7272 | 0.7024 | 0.6776 | 0.6528 | 0.628 | 1.263 | 45 | 1.263 | 45
9.4 | 1.068 |  |  |  | 7.4 | 1.9175 | 1.8253 | 1.7331 | 1.6409 | 1.5488 | 1.4566 | 1.4187 | 1.3809 | 1.343 | 1.3052 | 1.2673 | 1.2185 | 1.1697 | 1.1209 | 1.0721 | 1.0233 | 0.98467 | 0.946 | 0.90733 | 0.86867 | 0.83 | 0.8152 | 0.8004 | 0.7856 | 0.7708 | 0.756 | 0.73093 | 0.70587 | 0.6808 | 0.65573 | 0.63067 | 1.2673 | 46 | 1.2673 | 46
9.5 | 1.07 |  |  |  | 7.5 | 1.9259 | 1.8329 | 1.74 | 1.647 | 1.5541 | 1.4611 | 1.4232 | 1.3853 | 1.3475 | 1.3096 | 1.2717 | 1.2227 | 1.1737 | 1.1247 | 1.0757 | 1.0267 | 0.98833 | 0.95 | 0.91167 | 0.87333 | 0.835 | 0.82 | 0.805 | 0.79 | 0.775 | 0.76 | 0.73467 | 0.70933 | 0.684 | 0.65867 | 0.63333 | 1.2717 | 47 | 1.2717 | 47
9.6 | 1.072 |  |  |  | 7.6 | 1.9342 | 1.8405 | 1.7468 | 1.6531 | 1.5594 | 1.4657 | 1.4277 | 1.3898 | 1.3519 | 1.3139 | 1.276 | 1.2268 | 1.1776 | 1.1284 | 1.0792 | 1.03 | 0.992 | 0.954 | 0.916 | 0.878 | 0.84 | 0.8248 | 0.8096 | 0.7944 | 0.7792 | 0.764 | 0.7384 | 0.7128 | 0.6872 | 0.6616 | 0.636 | 1.276 | 48 | 1.276 | 48
9.7 | 1.074 |  |  |  | 7.7 | 1.9426 | 1.8481 | 1.7537 | 1.6592 | 1.5647 | 1.4702 | 1.4322 | 1.3943 | 1.3563 | 1.3183 | 1.2803 | 1.2309 | 1.1815 | 1.1321 | 1.0827 | 1.0333 | 0.99567 | 0.958 | 0.92033 | 0.88267 | 0.845 | 0.8296 | 0.8142 | 0.7988 | 0.7834 | 0.768 | 0.74213 | 0.71627 | 0.6904 | 0.66453 | 0.63867 | 1.2803 | 49 | 1.2803 | 49
9.8 | 1.076 |  |  |  | 7.8 | 1.951 | 1.8557 | 1.7605 | 1.6653 | 1.57 | 1.4748 | 1.4368 | 1.3987 | 1.3607 | 1.3227 | 1.2847 | 1.2351 | 1.1855 | 1.1359 | 1.0863 | 1.0367 | 0.99933 | 0.962 | 0.92467 | 0.88733 | 0.85 | 0.8344 | 0.8188 | 0.8032 | 0.7876 | 0.772 | 0.74587 | 0.71973 | 0.6936 | 0.66747 | 0.64133 | 1.2847 | 50 | 1.2847 | 50
9.9 | 1.078 |  |  |  | 7.9 | 1.9594 | 1.8634 | 1.7673 | 1.6713 | 1.5753 | 1.4793 | 1.4413 | 1.4032 | 1.3651 | 1.3271 | 1.289 | 1.2392 | 1.1894 | 1.1396 | 1.0898 | 1.04 | 1.003 | 0.966 | 0.929 | 0.892 | 0.855 | 0.8392 | 0.8234 | 0.8076 | 0.7918 | 0.776 | 0.7496 | 0.7232 | 0.6968 | 0.6704 | 0.644 | 1.289 | 51 | 1.289 | 51
10 | 1.08 |  |  |  | 8 | 1.9677 | 1.871 | 1.7742 | 1.6774 | 1.5806 | 1.4839 | 1.4458 | 1.4077 | 1.3695 | 1.3314 | 1.2933 | 1.2433 | 1.1933 | 1.1433 | 1.0933 | 1.0433 | 1.0067 | 0.97 | 0.93333 | 0.89667 | 0.86 | 0.844 | 0.828 | 0.812 | 0.796 | 0.78 | 0.75333 | 0.72667 | 0.7 | 0.67333 | 0.64667 | 1.2933 | 52 | 1.2933 | 52
10.1 | 1.082 |  |  |  | 8.1 | 1.9761 | 1.8786 | 1.781 | 1.6835 | 1.586 | 1.4884 | 1.4503 | 1.4121 | 1.374 | 1.3358 | 1.2977 | 1.2475 | 1.1973 | 1.1471 | 1.0969 | 1.0467 | 1.0103 | 0.974 | 0.93767 | 0.90133 | 0.865 | 0.8488 | 0.8326 | 0.8164 | 0.8002 | 0.784 | 0.75707 | 0.73013 | 0.7032 | 0.67627 | 0.64933 | 1.2977 | 53 | 1.2977 | 53
10.2 | 1.084 |  |  |  | 8.2 | 1.9845 | 1.8862 | 1.7879 | 1.6896 | 1.5913 | 1.493 | 1.4548 | 1.4166 | 1.3784 | 1.3402 | 1.302 | 1.2516 | 1.2012 | 1.1508 | 1.1004 | 1.05 | 1.014 | 0.978 | 0.942 | 0.906 | 0.87 | 0.8536 | 0.8372 | 0.8208 | 0.8044 | 0.788 | 0.7608 | 0.7336 | 0.7064 | 0.6792 | 0.652 | 1.302 | 54 | 1.302 | 54
10.3 | 1.086 |  |  |  | 8.3 | 1.9929 | 1.8938 | 1.7947 | 1.6956 | 1.5966 | 1.4975 | 1.4593 | 1.421 | 1.3828 | 1.3446 | 1.3063 | 1.2557 | 1.2051 | 1.1545 | 1.1039 | 1.0533 | 1.0177 | 0.982 | 0.94633 | 0.91067 | 0.875 | 0.8584 | 0.8418 | 0.8252 | 0.8086 | 0.792 | 0.76453 | 0.73707 | 0.7096 | 0.68213 | 0.65467 | 1.3063 | 55 | 1.3063 | 55
10.4 | 1.088 |  |  |  | 8.4 | 2.0012 | 1.9014 | 1.8016 | 1.7017 | 1.6019 | 1.5021 | 1.4638 | 1.4255 | 1.3872 | 1.3489 | 1.3107 | 1.2599 | 1.2091 | 1.1583 | 1.1075 | 1.0567 | 1.0213 | 0.986 | 0.95067 | 0.91533 | 0.88 | 0.8632 | 0.8464 | 0.8296 | 0.8128 | 0.796 | 0.76827 | 0.74053 | 0.7128 | 0.68507 | 0.65733 | 1.3107 | 56 | 1.3107 | 56
10.5 | 1.09 |  |  |  | 8.5 | 2.0096 | 1.909 | 1.8084 | 1.7078 | 1.6072 | 1.5066 | 1.4683 | 1.43 | 1.3916 | 1.3533 | 1.315 | 1.264 | 1.213 | 1.162 | 1.111 | 1.06 | 1.025 | 0.99 | 0.955 | 0.92 | 0.885 | 0.868 | 0.851 | 0.834 | 0.817 | 0.8 | 0.772 | 0.744 | 0.716 | 0.688 | 0.66 | 1.315 | 57 | 1.315 | 57
10.6 | 1.092 |  |  |  | 8.6 | 2.018 | 1.9166 | 1.8152 | 1.7139 | 1.6125 | 1.5111 | 1.4728 | 1.4344 | 1.3961 | 1.3577 | 1.3193 | 1.2681 | 1.2169 | 1.1657 | 1.1145 | 1.0633 | 1.0287 | 0.994 | 0.95933 | 0.92467 | 0.89 | 0.8728 | 0.8556 | 0.8384 | 0.8212 | 0.804 | 0.77573 | 0.74747 | 0.7192 | 0.69093 | 0.66267 | 1.3193 | 58 | 1.3193 | 58
10.7 | 1.094 |  |  |  | 8.7 | 2.0263 | 1.9242 | 1.8221 | 1.72 | 1.6178 | 1.5157 | 1.4773 | 1.4389 | 1.4005 | 1.3621 | 1.3237 | 1.2723 | 1.2209 | 1.1695 | 1.1181 | 1.0667 | 1.0323 | 0.998 | 0.96367 | 0.92933 | 0.895 | 0.8776 | 0.8602 | 0.8428 | 0.8254 | 0.808 | 0.77947 | 0.75093 | 0.7224 | 0.69387 | 0.66533 | 1.3237 | 59 | 1.3237 | 59
10.8 | 1.096 |  |  |  | 8.8 | 2.0347 | 1.9318 | 1.8289 | 1.726 | 1.6231 | 1.5202 | 1.4818 | 1.4433 | 1.4049 | 1.3664 | 1.328 | 1.2764 | 1.2248 | 1.1732 | 1.1216 | 1.07 | 1.036 | 1.002 | 0.968 | 0.934 | 0.9 | 0.8824 | 0.8648 | 0.8472 | 0.8296 | 0.812 | 0.7832 | 0.7544 | 0.7256 | 0.6968 | 0.668 | 1.328 | 60 | 1.328 | 60
10.9 | 1.098 |  |  |  | 8.9 | 2.0431 | 1.9394 | 1.8358 | 1.7321 | 1.6284 | 1.5248 | 1.4863 | 1.4478 | 1.4093 | 1.3708 | 1.3323 | 1.2805 | 1.2287 | 1.1769 | 1.1251 | 1.0733 | 1.0397 | 1.006 | 0.97233 | 0.93867 | 0.905 | 0.8872 | 0.8694 | 0.8516 | 0.8338 | 0.816 | 0.78693 | 0.75787 | 0.7288 | 0.69973 | 0.67067 | 1.3323 | 61 | 1.3323 | 61
11 | 1.1 |  |  |  | 9 | 2.0515 | 1.947 | 1.8426 | 1.7382 | 1.6338 | 1.5293 | 1.4908 | 1.4523 | 1.4137 | 1.3752 | 1.3367 | 1.2847 | 1.2327 | 1.1807 | 1.1287 | 1.0767 | 1.0433 | 1.01 | 0.97667 | 0.94333 | 0.91 | 0.892 | 0.874 | 0.856 | 0.838 | 0.82 | 0.79067 | 0.76133 | 0.732 | 0.70267 | 0.67333 | 1.3367 | 62 | 1.3367 | 62
11.1 | 1.102 |  |  |  | 9.1 | 2.0598 | 1.9546 | 1.8495 | 1.7443 | 1.6391 | 1.5339 | 1.4953 | 1.4567 | 1.4182 | 1.3796 | 1.341 | 1.2888 | 1.2366 | 1.1844 | 1.1322 | 1.08 | 1.047 | 1.014 | 0.981 | 0.948 | 0.915 | 0.8968 | 0.8786 | 0.8604 | 0.8422 | 0.824 | 0.7944 | 0.7648 | 0.7352 | 0.7056 | 0.676 | 1.341 | 63 | 1.341 | 63
11.2 | 1.104 |  |  |  | 9.2 | 2.0682 | 1.9623 | 1.8563 | 1.7503 | 1.6444 | 1.5384 | 1.4998 | 1.4612 | 1.4226 | 1.384 | 1.3453 | 1.2929 | 1.2405 | 1.1881 | 1.1357 | 1.0833 | 1.0507 | 1.018 | 0.98533 | 0.95267 | 0.92 | 0.9016 | 0.8832 | 0.8648 | 0.8464 | 0.828 | 0.79813 | 0.76827 | 0.7384 | 0.70853 | 0.67867 | 1.3453 | 64 | 1.3453 | 64
11.3 | 1.106 |  |  |  | 9.3 | 2.0766 | 1.9699 | 1.8631 | 1.7564 | 1.6497 | 1.543 | 1.5043 | 1.4657 | 1.427 | 1.3883 | 1.3497 | 1.2971 | 1.2445 | 1.1919 | 1.1393 | 1.0867 | 1.0543 | 1.022 | 0.98967 | 0.95733 | 0.925 | 0.9064 | 0.8878 | 0.8692 | 0.8506 | 0.832 | 0.80187 | 0.77173 | 0.7416 | 0.71147 | 0.68133 | 1.3497 | 65 | 1.3497 | 65
11.4 | 1.108 |  |  |  | 9.4 | 2.085 | 1.9775 | 1.87 | 1.7625 | 1.655 | 1.5475 | 1.5088 | 1.4701 | 1.4314 | 1.3927 | 1.354 | 1.3012 | 1.2484 | 1.1956 | 1.1428 | 1.09 | 1.058 | 1.026 | 0.994 | 0.962 | 0.93 | 0.9112 | 0.8924 | 0.8736 | 0.8548 | 0.836 | 0.8056 | 0.7752 | 0.7448 | 0.7144 | 0.684 | 1.354 | 66 | 1.354 | 66
11.5 | 1.11 |  |  |  | 9.5 | 2.0933 | 1.9851 | 1.8768 | 1.7686 | 1.6603 | 1.5521 | 1.5133 | 1.4746 | 1.4358 | 1.3971 | 1.3583 | 1.3053 | 1.2523 | 1.1993 | 1.1463 | 1.0933 | 1.0617 | 1.03 | 0.99833 | 0.96667 | 0.935 | 0.916 | 0.897 | 0.878 | 0.859 | 0.84 | 0.80933 | 0.77867 | 0.748 | 0.71733 | 0.68667 | 1.3583 | 67 | 1.3583 | 67
11.6 | 1.112 |  |  |  | 9.6 | 2.1017 | 1.9927 | 1.8837 | 1.7747 | 1.6656 | 1.5566 | 1.5178 | 1.479 | 1.4402 | 1.4015 | 1.3627 | 1.3095 | 1.2563 | 1.2031 | 1.1499 | 1.0967 | 1.0653 | 1.034 | 1.0027 | 0.97133 | 0.94 | 0.9208 | 0.9016 | 0.8824 | 0.8632 | 0.844 | 0.81307 | 0.78213 | 0.7512 | 0.72027 | 0.68933 | 1.3627 | 68 | 1.3627 | 68
11.7 | 1.114 |  |  |  | 9.7 | 2.1101 | 2.0003 | 1.8905 | 1.7807 | 1.6709 | 1.5612 | 1.5223 | 1.4835 | 1.4447 | 1.4058 | 1.367 | 1.3136 | 1.2602 | 1.2068 | 1.1534 | 1.1 | 1.069 | 1.038 | 1.007 | 0.976 | 0.945 | 0.9256 | 0.9062 | 0.8868 | 0.8674 | 0.848 | 0.8168 | 0.7856 | 0.7544 | 0.7232 | 0.692 | 1.367 | 69 | 1.367 | 69
11.8 | 1.116 |  |  |  | 9.8 | 2.1185 | 2.0079 | 1.8974 | 1.7868 | 1.6763 | 1.5657 | 1.5268 | 1.488 | 1.4491 | 1.4102 | 1.3713 | 1.3177 | 1.2641 | 1.2105 | 1.1569 | 1.1033 | 1.0727 | 1.042 | 1.0113 | 0.98067 | 0.95 | 0.9304 | 0.9108 | 0.8912 | 0.8716 | 0.852 | 0.82053 | 0.78907 | 0.7576 | 0.72613 | 0.69467 | 1.3713 | 70 | 1.3713 | 70
11.9 | 1.118 |  |  |  | 9.9 | 2.1268 | 2.0155 | 1.9042 | 1.7929 | 1.6816 | 1.5703 | 1.5313 | 1.4924 | 1.4535 | 1.4146 | 1.3757 | 1.3219 | 1.2681 | 1.2143 | 1.1605 | 1.1067 | 1.0763 | 1.046 | 1.0157 | 0.98533 | 0.955 | 0.9352 | 0.9154 | 0.8956 | 0.8758 | 0.856 | 0.82427 | 0.79253 | 0.7608 | 0.72907 | 0.69733 | 1.3757 | 71 | 1.3757 | 71
12 | 1.12 |  |  |  | 10 | 2.1352 | 2.0231 | 1.911 | 1.799 | 1.6869 | 1.5748 | 1.5358 | 1.4969 | 1.4579 | 1.419 | 1.38 | 1.326 | 1.272 | 1.218 | 1.164 | 1.11 | 1.08 | 1.05 | 1.02 | 0.99 | 0.96 | 0.94 | 0.92 | 0.9 | 0.88 | 0.86 | 0.828 | 0.796 | 0.764 | 0.732 | 0.7 | 1.38 | 72 | 1.38 | 72
12.1 | 1.121
12.2 | 1.122
12.3 | 1.123 | [35 empty] | Max | 1.38 | Max | 1.38
12.4 | 1.124 | [35 empty] | Min | 1 | Min | 1
12.5 | 1.125
12.6 | 1.126
12.7 | 1.127
12.8 | 1.128
12.9 | 1.129
13 | 1.13
13.1 | 1.132
13.2 | 1.134
13.3 | 1.136
13.4 | 1.138
13.5 | 1.14
13.6 | 1.142
13.7 | 1.144
13.8 | 1.146
13.9 | 1.148
14 | 1.15
14.1 | 1.151
14.2 | 1.152
14.3 | 1.153
14.4 | 1.154
14.5 | 1.155
14.6 | 1.156
14.7 | 1.157
14.8 | 1.158
14.9 | 1.159
15 | 1.16
15.1 | 1.161
15.2 | 1.162
15.3 | 1.163
15.4 | 1.164
15.5 | 1.165
15.6 | 1.166
15.7 | 1.167
15.8 | 1.168
15.9 | 1.169
16 | 1.17
Ambient Vs PDP
Ambient Temp (°C) | RH = 26% | Row number for water content
10 | -8 | 65
12 | -6 | 67
14 | -5 | 68
16 | -3 | 70
18 | -2 | 71
20 | 0 | 73
22 | 1 | 74
24 | 3 | 76
26 | 4 | 77
28 | 6 | 79
30 | 8 | 81
32 | 9 | 82
34 | 11 | 84
36 | 13 | 86
38 | 14 | 87
40 | 16 | 89
42 | 18 | 91
44 | 19 | 92
46 | 21 | 94
48 | 23 | 96
50 | 24 | 97
52 | 26 | 99
54 | 28 | 101
56 | 29 | 102

## Machines
Type | bar | psi | l/s | m³/hr | cfm | W 50Hz | W 60Hz | V/Hz/Ph 50 | V/Hz/Ph 60 | Connection | L mm | W mm | H mm | Kg | gas | P Drop | Ceccato Type
FX 1 | 13 | 188.5 | 5.8333 | 21 | 12.3667 |  |  | 230/1/50 | 115-230/1/60 | 3/4" | 500 | 350 | 484 | 19 | R134a | 0.15 | A0
FX 2 | 13 | 188.5 | 10 | 36 | 21.2 |  |  | 230/1/50 | 115-230/1/60 | 3/4" | 500 | 350 | 484 | 19 | R134a | 0.25 | A1
FX 3 | 13 | 188.5 | 14.1667 | 51 | 30.0333 |  |  | 230/1/50 | 115-230/1/60 | 3/4" | 500 | 350 | 484 | 20 | R134a | 0.25 | A2
FX 4 | 13 | 188.5 | 20 | 72 | 42.4 |  |  | 230/1/50 | 115-230/1/60 | 3/4" | 500 | 350 | 484 | 25 | R134a | 0.25 | A3
FX 5 | 13 | 188.5 | 30.4167 | 109.5 | 64.4833 |  |  | 230/1/50 | 115-230/1/60 | 3/4" | 500 | 350 | 484 | 27 | R134a | 0.3 | A4
FX 6 | 13 | 188.5 | 39.1667 | 141 | 83.0333 |  |  | 230/1/50 | 115-230/1/60 | 1" | 500 | 370 | 804 | 51 | R404A | 0.32 | A5
FX 7 | 13 | 188.5 | 50 | 180 | 106 |  |  | 230/1/50 | 115-230/1/60 | 1" | 500 | 370 | 804 | 51 | R404A | 0.38 | A6
FX 8 | 13 | 188.5 | 60 | 216 | 127.2 |  |  | 230/1/50 | 115-230/1/60 | 1 1/2" | 560 | 460 | 829 | 61 | R404A | 0.18 | A7
FX 9 | 13 | 188.5 | 68.3333 | 246 | 144.8667 |  |  | 230/1/50 | 115-230/1/60 | 1 1/2" | 560 | 460 | 829 | 68 | R404A | 0.25 | A7.5
FX 10 | 13 | 188.5 | 86.6667 | 312 | 183.7333 |  |  | 230/1/50 | 115-230/1/60 | 1 1/2" | 560 | 460 | 829 | 73 | R404A | 0.18 | A8
FX 11 | 13 | 188.5 | 108.3333 | 390 | 229.6667 |  |  | 230/1/50 | 230/1/60 | 1 1/2" | 560 | 580 | 939 | 90 | R404A | 0.2 | A9
FX 12 | 13 | 188.5 | 128.3333 | 462 | 272.0667 |  |  | 230/1/50 | 230/1/60 | 1 1/2" | 560 | 580 | 939 | 90 | R404A | 0.27 | A10
FX 13 | 16 | 232 | 165 | 594 | 349.8 |  |  | 230/1/50 | 230/1/60 | 2 1/2" | 975 | 795 | 925 | 178 | R404A | 0.25 | DLX100
FX 14 | 16 | 232 | 200 | 720 | 424 |  |  | 230/1/50 | 230/1/60 | 2 1/2" | 975 | 795 | 925 | 178 | R404A | 0.25 | DLX120
FX 15 | 16 | 232 | 232 | 835.2 | 491.84 |  |  | 400/3/50 | 460/3/60 | 2 1/2" | 975 | 795 | 925 | 183 | R404A | 0.35 | DLX140
Select Link | 2
PDP | TRUE
Machine | FALSE
PDP Requirement | 30
Selected Machine | FX 11
Performance Lookup
FX 15 | 16 | 232 | 232
FX 14 | 16 | 232 | 200
FX 13 | 16 | 232 | 165
FX 12 | 13 | 188.5 | 128.3333
FX 11 | 13 | 188.5 | 108.3333
FX 10 | 13 | 188.5 | 86.6667
FX 9 | 13 | 188.5 | 68.3333
FX 8 | 13 | 188.5 | 60
FX 7 | 13 | 188.5 | 50
FX 6 | 13 | 188.5 | 39.1667
FX 5 | 13 | 188.5 | 30.4167
FX 4 | 13 | 188.5 | 20
FX 3 | 13 | 188.5 | 14.1667
FX 2 | 13 | 188.5 | 10
FX 1 | 13 | 188.5 | 5.8333

## Water Content (hidden)
Dewpoint | Dampspanning | Ammount of
°C | mbar | gr/m³
-70 | 0.002615 | 0.0027919
-69 | 0.003032 | 0.0032212
-68 | 0.003511 | 0.0037119
-67 | 0.00406 | 0.0042715
-66 | 0.004688 | 0.0049084
-65 | 0.005406 | 0.0056329
-64 | 0.006225 | 0.0064553
-63 | 0.007159 | 0.0073885
-62 | 0.008223 | 0.0084464
-61 | 0.009432 | 0.0096425
-60 | 0.0108 | 0.010989
-59 | 0.01236 | 0.012518
-58 | 0.01413 | 0.014244
-57 | 0.01612 | 0.016175
-56 | 0.01838 | 0.018357
-55 | 0.02092 | 0.020798
-54 | 0.0238 | 0.023553
-53 | 0.02703 | 0.026628
-52 | 0.003067 | 0.0030078
-51 | 0.03476 | 0.033935
-50 | 0.03935 | 0.038244
-49 | 0.04449 | 0.043046
-48 | 0.05026 | 0.048413
-47 | 0.05671 | 0.054384
-46 | 0.06393 | 0.061038
-45 | 0.07198 | 0.068423
-44 | 0.08097 | 0.076632
-43 | 0.09098 | 0.085732
-42 | 0.1021 | 0.095794
-41 | 0.1145 | 0.10696
-40 | 0.1283 | 0.11934
-39 | 0.1436 | 0.133
-38 | 0.1606 | 0.14812
-37 | 0.1794 | 0.16475
-36 | 0.2002 | 0.18308
-35 | 0.2233 | 0.20335
-34 | 0.2488 | 0.22562
-33 | 0.2769 | 0.25005
-32 | 0.3079 | 0.27689
-31 | 0.3421 | 0.30638
-30 | 0.3798 | 0.33874
-29 | 0.4213 | 0.37422
-28 | 0.4669 | 0.41303
-27 | 0.517 | 0.45549
-26 | 0.572 | 0.5019
-25 | 0.6323 | 0.55258
-24 | 0.6985 | 0.60798
-23 | 0.7709 | 0.66831
-22 | 0.8502 | 0.73412
-21 | 0.937 | 0.80586
-20 | 1.032 | 0.88406
-19 | 1.135 | 0.96847
-18 | 1.248 | 1.0607
-17 | 1.371 | 1.1607
-16 | 1.506 | 1.27
-15 | 1.652 | 1.3878
-14 | 1.811 | 1.5154
-13 | 1.984 | 1.6538
-12 | 2.172 | 1.8036
-11 | 2.376 | 1.9655
-10 | 2.597 | 2.1401
-9 | 2.837 | 2.329
-8 | 3.097 | 2.5329
-7 | 3.379 | 2.7531
-6 | 3.685 | 2.9912
-5 | 4.015 | 3.2469
-4 | 4.372 | 3.5225
-3 | 4.757 | 3.8185
-2 | 5.173 | 4.1371
-1 | 5.623 | 4.4804
0 | 6.108 | 4.8491
1 | 6.566 | 5.1937
2 | 7.055 | 5.5602
3 | 7.575 | 5.9483
4 | 8.129 | 6.3603
5 | 8.719 | 6.7974
6 | 9.347 | 7.2609
7 | 10.01 | 7.7482
8 | 10.72 | 8.2682
9 | 11.47 | 8.8153
10 | 12.27 | 9.3968
11 | 13.12 | 10.0124
12 | 14.02 | 10.6617
13 | 14.97 | 11.3443
14 | 15.98 | 12.0675
15 | 17.04 | 12.8233
16 | 18.17 | 13.6263
17 | 19.37 | 14.4762
18 | 20.63 | 15.3649
19 | 21.96 | 16.2994
20 | 23.373 | 17.289
21 | 24.86 | 18.3264
22 | 26.43 | 19.4177
23 | 28.086 | 20.5646
24 | 29.831 | 21.7688
25 | 31.671 | 23.0339
26 | 33.608 | 24.3609
27 | 35.649 | 25.7542
28 | 37.796 | 27.2146
29 | 40.055 | 28.7457
30 | 42.43 | 30.3496
31 | 44.927 | 32.0299
32 | 47.551 | 33.7895
33 | 50.307 | 35.6311
34 | 53.2 | 37.5574
35 | 56.237 | 39.5725
36 | 59.422 | 41.6784
37 | 62.762 | 43.8791
38 | 66.264 | 46.1785
39 | 69.934 | 48.5799
40 | 73.777 | 51.0857
41 | 77.8 | 53.6998
42 | 82.02 | 56.4328
43 | 86.42 | 59.272
44 | 91.03 | 62.2369
45 | 95.86 | 65.333
46 | 100.9 | 68.5524
47 | 106.2 | 71.9278
48 | 111.7 | 75.4172
49 | 117.4 | 79.0196
50 | 123.4 | 82.8009
51 | 129.7 | 86.7596
52 | 136.2 | 90.8272
53 | 143 | 95.0694
54 | 150.1 | 99.4845
55 | 157.5 | 104.0709
56 | 165.2 | 108.827
57 | 173.2 | 113.7513
58 | 181.5 | 118.8423
59 | 190.2 | 124.1638
60 | 199.2 | 129.6485
61 | 208.6 | 135.36
62 | 218.4 | 141.2961
63 | 228.5 | 147.3904
64 | 239.1 | 153.7702
65 | 250.1 | 160.3686
66 | 261.5 | 167.1839
67 | 273.3 | 174.214
68 | 285.6 | 181.5207
69 | 298.4 | 189.1016
70 | 311.6 | 196.8909